## Input
A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P
Technology /Size Category | CHP Technology /Size | Design Heat to Power Ratio | Minimum Electricity Capacity in CHP Mode | Minimum Thermal Output Capacity | Electricity Efficiency in Condensing Mode | Z-Ratio (Heat/Power Reduction) | Electrical Efficiency in CHP Mode | Capex A Multiplier (if CCGT in Condensing Mode) | Capex n Exponent | Opex £/MWhe (if CCGT in Condensing Mode) | Turbine Replacement as Percentage of Original Capex in Year 10 |  | Maximum Electrical Capacity in CHP Mode | Maximum Thermal Output Capacity | Maximum Fuel Input = Thermal Input
|  |  | MWe | MWt | % (GCV) |  | % (GCV) | £/kWe |  | £/MWhe | % |  | MWe | MWt | MWf (GCV)
1 | Small OCGT | 1.6 | 3.7 | 5.92 | N/A | N/A | 30% | 1759.6623 | -0.23 | 9.834 | 50% |  | 5.25 | 8.4 | 17.5
2 | Large OCGT | 1.2 | 7 | 8.4 | N/A | N/A | 35% | 1759.6623 | -0.23 | 8.7414 | 50% |  | 25.3333 | 30.4 | 72.381
3 | Small CCGT | 0.76 | 40 | 30.4 | 45.07% | 4.5 | 38.56% | 1376.7666 | -0.1 | 6.556 | 33.33% |  | 171.1027 | 130.038 | 443.787
4 | Large CCGT | 0.76 | 171.1027 | 130.038 | 45.07% | 4.5 | 38.56% | 808.5772 | 0 | 6.556 | 33.33% |  | No Max | No Max | No Max
Typical standard non-CHP boiler efficiency | CHP Asset life | Annual Operation Hours | Average Heat Load
[6 empty] | 2 | Participant to define
Key
% | Yrs | Hrs/Yr | MWt |  |  | 2 | Regulatory prescribed
80% | 20 | 6500 | 10

## Output
A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R
Results for Live Scenario
Thermal Output Capacity | Equivalent Thermal Input if standard boiler set to generate the Thermal Capacity | Technology /Size Cat | CHP Technology /Size | Elec Capacity in CHP Mode | Elec Capacity (if CCGT, in Condensing Mode) | CHP Capex per Unit Electrical Capacity (if CCGT, in Condensing Mode) | CHP Capex | CHP Capex per Unit Thermal Output Capacity | Actual Elec Generated = Elec. Capacity in CHP Mode x number of hours per year | Elec Generated (if CCGT elec which would be generated in Condensing Mode) | Opex (Operation and Maintenance) | Fuel Input (Thermal Input) | Turbine Replacement Cost | Additional equivalent OPEX to pay for a major Industrial CHP overall spread over the life of the asset |  | Fuel Input if standard boiler set to generate the Thermal Capacity | Additional Fuel required
MWt | MWt |  |  | MWe | MWe | £ / kWe | £ million | £ million / MWt | MWh/Yr | MWh/Yr | £ million /Yr | MWh (GCV) | £ million | £ million |  | MWh (GCV) | MWh
10 | 12.5 | 2 | Large OCGT | 8.3333 | 8.3333 | 1080.5404 | 9.0045 | 0.90045 | 54166.6667 | 54166.6667 | 0.47349 | 154761.9048 | 4.5023 | 0.22511 |  | 81250 | 73511.9048