## Cover Page
Version 20.1
Notes:
This template may require adjustments by individual operators to meet specific reporting requirements as defined in the site Permit(s)
Annual Performance Report 2021
Permit EPR/BJ7786IV
Integra North Energy Recovery Facility
Chineham ERF
Veolia
Year: | 2021
Address: | Whitmarsh Lane, Chineham Basingstoke, Hampshire RG24 8LL
Tel: | 020 7812 5000
Email:
Prepared by: | N Gronn | Position: | Technician
Approved by: | S McCluskey | Position: | Facility Manager
Version: | 1
Issue Date: | 2022-01-01

## Contents
Annual Performance Report 2021 |  | Integra North Energy Recovery Facility
Contents |  |  |  | Notes:
Section | Subject |  | Page | Section references and Page nos. to be inserted
| Facility Information |  |  | Sections and Subjects may require adjustment by individual operators to meet specific reporting requirements as defined in the sites Permit(s)
Operational Summary
Operational Data
Performance Form 1
Energy Form 1
Permit Compliance
Improvements
Public Liaison
Residue Quality - Optional
Emissions to Water
Emissions to Air (periodically monitored)
Emissions to Air (continuously monitored)
Hydrogen Chloride emissions
Sulphur Dioxide emissions
Oxides of Nitrogen emissions
Total Organic Carbon emissions
Particulate Matter emissions
Carbon Monoxide emissions
Ammonia emissions
Version Control
Section | Information |  | Date
Distribution
Copy | Name, Role |  | No.
This report is required under the Industrial Emissions Directive Article 55(2) requirements on reporting and public information on waste incineration plants and co-incineration plants, which require the operator to produce an annual report on the functioning and monitoring of the plant and make it available to the public.

## Facility Info
Annual Performance Report 2021 | Integra North Energy Recovery Facility
Plant Description and Design |  | Notes:
Chineham ERF was the first of its kind to be built in Hampshire and is a leading example of best environmental practice for waste treatment. Waste produced by Basingstoke and Dean, and the North Hampshire Districts is processed at this ERF, providing a long term, sustainable solution for waste recovery. It recovers heat energy from the waste to produce steam, which is used to generate electricity supplied to the National Grid. Strict environmental controls and proven operating experience ensure the Chineham ERF is a centre of excellence and a benchmark for the industry. Technical details of the plant: Maximum Permitted Refuse throughput – 110,000 tonnes per annum, with approximately 13 tonnes per hour burning capacity per stream Storage capacity – four days full plant capacity Number of tipping bays – 5 Steam output – 38 tonnes of steam per hour at 400*C and 45 bar Flue gas treatment – CNIM semi-dry lime scrubber followed by high performance bag filters, discharging into a 65 metre high chimney Energy produced – maximum generating capacity 9MW |  | Include summary of plant design, design capacity, no. of combustion lines, electrical and heat capacity and any other general information that describes the facility, its location and purpose
Summary of Operational Processes and Procedures
The Chineham ERF forms part of Veolia’s Integrated Contracts, the most progressive integrated waste management system in Britain which provides sustainable waste management for all the domestic waste in the county. The ERF is regulated by the Environment Agency and is certified in compliance with: ISO 9001 : 2008 ISO 14001 : 2004, OHAS 18001 : 2007, and ISO 25999 Solid Residue Outputs The Incinerator Bottom Ash (IBA) is transported by Veolia Haulage to an aggregate processing facility situated in Longparish, Hampshire. The IBA is reprocessed into a number of different graded aggregates, ferrous and non ferrous metal products, which are then utilised in the construction and metal industry. Ferrous metals removed during on site processing of IBA are forwarded to a recycling facility. The metals are separated into individual fractions, and are sent on for utilisation in the metal industry. The fine particulate matter, known as Air Pollution Control Residue (APCr), is removed from the process by a fabric filter. The APCr is sent to Empire, another Veolia site located in Aldridge, West Midlands where it is used to neutralise spent acid wastes before final disposal. Water Discharges from Site The water required for plant operations is reused extensively within the process and therefore few, or no water discharges are released from the facility. When required, water discharges are released in batches from the plant in accordance with the Permit. Samples are taken and analysed for the parameters listed in the Trade Effluent Discharge Consent issued and regulated by Thames Water. Flue Gasses All gaseous emissions generated during the combustion process pass through an extensive flue gas cleaning process which begins in the boiler itself where good combustion conditions are maintained and Urea is added to treat oxides of nitrogen. Gasses exit the boiler and enter a gas scrubber where hydrated lime is injected to neutralise acid gasses, activated carbon is added to remove metals and dioxins, and finally gasses pass through the bag filter house to remove any remaining particulates. The cleaned gasses are finally released into the atmosphere through the chimney stacks. In compliance with the IED and EPR Permit requirements, the flue gasses are continuously monitored using MCERTS accredited equipment. In addition to the continuous monitoring, an extractive sampling campaign is undertaken bi-annually by an approved service supplier. The organisation used for analysis and monitoring are accredited by the United Kingdom Accreditation Service (UKAS) and the Environment Agency’s Monitoring Certification Scheme (Mcerts). |  | Include summary of key processes and procedures such as (but not limited to); waste reception, control rooms, grate, bed and boiler, energy & heat generation, cooling systems, residue management, emission controls, health and safety systems, maintenance

## Operational Data
Annual Performance Report 2021 |  |  |  | Integra North Energy Recovery Facility
Operational Data | [8 empty] | Notes:
Plant Size | 110000 |  | tonnes pa |  | MWth | 12 | MWe |  | * - RDF to include SRF
No. of combustion lines | 1 |  | No. of Turbines: |  | 1 |  |  |  | ** - CHP plants only
2020 updates include; heat in MWh, water in Litres, NCV in MJ/kg
Waste types received | Unit | Q1 | Q2 | Q3 | Q4 | Year Total | %
Household / Local Authority | tonnes | 22492 | 19950 | 19537 | 18870 | 80849 | 77.14% |  | Availability Definition: 'the availability of a line is to be calculated by the number of hours the line reported Continuously Monitored emission levels to the Regulator through the calendar year divided by the total number of hours in that year. The overall plant availability is calculated as the Mean of all lines in the plant. For clarity this includes periods of Other Than Normal Operating Conditions (OTNOC) and abnormal operation.' Rationale: The primary function of an Energy from Waste facility is the recovery of waste. It follows therefore that the availability of a plant is determined by the period of time a facility spends undertaking this activity.
Commercial & Industrial |  | 3892 | 6154 | 7329 | 8468 | 25843 | 24.66%
Hazardous | [5 empty] | 0 | -
Clinical (inc. Offensive) |  | 105 | 44 | 5 | 5 | 159 | 0.1517%
Waste wood (biomass) | [5 empty] | 0 | -
Refuse Derived Fuel * - H'hold/LA | [5 empty] | 0 | -
Refuse Derived Fuel * - C&I | [5 empty] | 0 | -
Other [Please specify] | [5 empty] | 0 | -
Other [Please specify]
Total waste received |  | 26489 | 26148 | 26871 | 27343 | 106851
Total waste combusted |  | 26155 | 25723 | 26431 | 26502 | 104811 | 98.09%
Rejected Waste | [5 empty] | 0 | -
Unprocessed waste transferred out | [5 empty] | 0 | -
Energy Usage / Export | Unit | Q1 | Q2 | Q3 | Q4 | Year Total | KWh/te
Power Generated | MWh | 16489 | 16013 | 15735 | 16193 | 64430 | 614.7256
Power Exported |  | 14277 | 13899 | 13691 | 14119 | 55986 | 534.1615
Power Used on site |  | 2212 | 2114 | 2044 | 2074 | 8444 | 80.5641
Power Imported |  | 2 | 2 | 2 | 22 | 28 | 0.26715
Parasitic Load | % | 13.43% | 13.21% | 13% | 12.93% | 13.14%
Thermal Energy Produced ** | MWh |  |  |  |  | 0 | -
Thermal Energy Exported ** | [5 empty] | 0 | -
R1 value |  | R1 |  |  |  | Design / Operational / n/a
Waste Disposal & Recovery | Unit | Q1 | Q2 | Q3 | Q4 | Year Total | % inputs
APC Residues - produced | tonnes | 715 | 658 | 631 | 633 | 2637 | 2.516%
IBA - produced |  | 4421 | 4529 | 4363 | 4164 | 17477 | 16.67%
Metals recycling |  | 439 | 413 | 398 | 398 | 1648 | 1.572%
Other |  | 0 | 0 | 0 | 0 | 0 | -
Other |  | 0 | 0 | 0 | 0 | 0 | -
Other |  | 0 | 0 | 0 | 0 | 0 | -
Raw Material Usage | Unit | Q1 | Q2 | Q3 | Q4 | Year Total | t or Ltr /te
Mains Water | ltrs | 6137 | 6549 | 7063 | 5916 | 25665 | 0.24487
Other Water | ltrs |  |  |  |  | 0 | -
Ammonia | kgs |  |  |  |  | 0 | -
Urea | t | 42 | 41 | 40 | 41 | 164 | 1.5647
Activated Carbon | t | 5 | 4 | 4 | 4 | 17 | 0.1622
Lime / hydrated lime | t | 218 | 209 | 178 | 187 | 792 | 7.5565
Fuel oil | ltrs | 1178 | -25 | 3252 | 15694 | 20099 | 0.19176
Gas | cf | 0 | 0 | 0 | 0 | 0
Other |  | 0 | 0 | 0 | 0 | 0
Summary | Line/Unit | Q1 | Q2 | Q3 | Q4 | Year Total |  | Hrs in year
Availability of waste combustion by line, hrs | 1 | 2160 | 2184 | 2206 | 2170 | 8720 | 99.54% | 8760
2
3
4
5
Overall Availability, mean avg. of all lines, hrs | [5 empty] | 8720 | 99.54%
Hours of turbine operations, hrs | 1 | 2160 | 2184 | 2208 | 2172 | 8724 | 99.59%
Hours of turbine operations, hrs | 2
Hours of heat / steam export | [6 empty] | n/a
Net Calorific Value of waste | MJ/kg
Abnormal Events | qty. | 0 | 0 | 0 | 0 | 0 | no
Abnormal operation | hours | 0 | 0 | 0 | 0 | 0 | 0%
Permit Breaches | qty. | 0 | 0 | 0 | 0 | 0 | no

## Operational Summary
Annual Performance Report 2021 | Integra North Energy Recovery Facility
Summary of Plant Operations and Maintenance during the reporting year |  | Notes:
There were no major component upgrades or replacements in 2021 and any maintenance was a-typical of the normal running of a waste incineration unit |  | Include summary of key operational and/or maintenance activity undertaken in the year, such as any major component upgrades and/or replacements
Summary of Residue Handling for the reporting year
The Incinerator Bottom Ash (IBA) is transported by Veolia Haulage to an aggregate processing facility situated in Longparish, Hampshire. The IBA is reprocessed into a number of different graded aggregates, ferrous and non ferrous metal products, which are then utilised in the construction and metal industry. Ferrous metals removed during on site processing of IBA are forwarded to a recycling facility. The metals are separated into individual fractions, and are sent on for utilisation in the metal industry. The fine particulate matter, known as Air Pollution Control Residue (APCr), is removed from the process by a fabric filter. The APCr is sent to Empire, another Veolia site located in Aldridge, West Midlands where it is used to neutralise spent acid wastes before final disposal. |  | Include in here a summary of residue handling regimes and destinations

## Perf. Form 1
2021 | Annual Reporting Performance Form 1
Permit EPR/BJ7786IV |  |  |  |  | Operator: | 0
Facility: | Integra North Energy Recovery Facility |  |  |  | Form: | Performance 1
Reporting Period from: |  |  | 01.01.2021 |  | to: | 31.12.2021
2021 | Annual Reporting of Waste Disposal and Recovery
Waste Description |  | Disposal Route(s) |  | Disposal Tonnes |  | Recovery Tonnes |  | % / tonne of waste incinerated
1) Hazardous Wastes
APC Residues |  | D9 |  | 2637 |  |  |  | 2.516%
IBA | [7 empty] | -
-
-
Total Hazardous Waste |  |  |  | 2637 |  | 0 |  | 2.516%
2) Non-Hazardous Wastes
IBA |  | R5 |  |  |  | 17477 |  | 16.67%
Ferrous Metal |  | R4 |  |  |  | 1648 |  | 1.572%
Process Water | [7 empty] | -
-
-
Total Non-Hazardous Waste |  |  |  | 0 |  | 19125 |  | 18.25%
TOTAL WASTE |  |  |  | 2637 |  | 19125 |  | 20.76%
Operator’s comments :
The APC residue is utilised at a specialist hazardous waste treatment facility where it is re-used to neutralise acid wastes before final disposal
2021 | Annual Reporting of Water and Other Raw Material Usage
Raw Material |  |  |  | Usage |  | Unit | Specific Usage |  | Unit
Mains Water |  |  |  | 25665 |  | m3 | 0.24487 |  | m3/te
Total Water |  |  |  | 25665 |  | m3 | 0.24487 |  | m3/te
Urea / Ammonia |  |  |  | 164000 |  | kg | 1.5647 |  | kg/te
Activated Carbon |  |  |  | 17000 |  | kg | 0.1622 |  | kg/te
Lime / hydrated lime / Sodium Bicarb. |  |  |  | 792000 |  | kg | 7.5565 |  | kg/te
Operator’s comments :
2021 | Annual Reporting of other performance indicators
Parameter |  | Results by Line
|  | A1 | A2 | A3 | A4 | A5 |  | Turbine 1 | Turbine 2
Operating hours for the year, hours |  | 8720 | [5 empty] | 8724
Number of periods of abnormal operation, qty. |  | 0
Cumulative hours of abnormal operation for this year, hours |  | 0
Operator’s comments :
Signed: | [5 empty] | Date: | 24th January 2022

## Energy Form 1
2021 | Annual Reporting of Energy Usage/Export
Permit EPR/BJ7786IV |  |  | Operator: | 0
Facility: | Integra North Energy Recovery Facility |  | Form: | Energy 1
Reporting Period from: |  | 01.01.2021 | to: | 31.12.2021
Energy Source |  | Energy Usage | Unit | Specific Usage (KWh/tonne incinerated)
Electricity Produced |  | 64430 | MWh | 614.7256
Electricity Imported |  | 28 | MWh | 0.26715
Electricity Exported |  | 55986 | MWh | 534.1615
Gas Oil |  | 20099 | Litres | 0.19176
Steam/hot water exported |  | 0 | GWh | -
Operator’s comments :
Signed: |  |  |  | Date: | 24th January 2022

## Ash 1
Annual Reporting of Ash Composition for the October to December 2021
Permit EPR/BJ7786IV | [5 empty] | Operator: | Veolia ES Hampshire Ltd
Facility: | Integra North Energy Recovery Facility | [5 empty] | Form: | Ash 1
[5 empty] | LOI % |  |  | & Carbon (TOC) w/w
| Bottom Ash |  |  |  | * |  |  | * 1.1
* At least one of LOI or TOC to be reported
Ash Composition - Metals
| Cd mg/kg | Sb mg/kg | Hg mg/kg | Tl mg/kg | Pb mg/kg | Cr mg/kg | Cu mg/kg | Mn mg/kg | Ni mg/kg | As mg/kg | Co mg/kg | V mg/kg | Zn mg/kg
Bottom Ash | 26.7 | 55.1 | <0.4 | <0.08 | 456 | 71.8 | 1820 | 474 | 80.7 | 5.04 | 26.8 | 15 | 1553
APC Residues | 166 | 536 | 6.1 | 0.5 | 721 | 72.2 | 469 | 426 | 49.4 | 35.3 | 10.1 | 11 | 8075
| Dioxin I-TEQ ng/kg |  |  |  | Dioxin WHO-TEQ ng/kg | [5 empty] | DIOXIN-LIKE PCBs ng/kg
[5 empty] | Humans/animals |  | Birds |  | Fish
Bottom Ash | 2.46 |  |  |  | 2.69 |  | 3.9 |  | 2.81 |  | 15.5
APC Residues | 243 |  |  |  | 237 |  | 506 |  | 267 |  | 178
Signed: | [6 empty] | Date: | 24th January 2022

## S3E1
Reporting of Energy Usage for the Period: January - December 2021
Permit EPR/BJ7786IV |  |  |  | Operator: | Veolia ES Hampshire Ltd
Facility: | Integra North Energy Recovery Facility |  |  |  | Form: | S3/E/1
Energy Source | Energy Usage Quantity | Primary Energy (MWh) | CO2 Produced Tonnes | Trends in Energy Usage Year Parameter
[5 empty] | Primary Energy usage | CO2 Produced | CO2 per unit output
|  |  |  | 2015 | 1903 | 315 | 0.16
Electricity* | 28 | 72 | 12 | 2016 | 3002 | 576 | 0.19
Gas Oil | 20 | 225 | 56.25 | 2017 | 660 | 109 | 0.19
|  |  |  | 2018 | 5166 | 861 | 0.19
TOTAL | 48 | 297 | 68.25 | 2019 | 7525 | 1364 | 0.18
|  |  |  | 2020 | 2042 | 436 | 0.21
* conversion factor for delivered electricity to primary energy =2.6 (import) 3.9 (export)
Operator's comments
Signed: |  |  |  |  | Date: | 24th January 2022

## S3WU1
Reporting of Water Usage for the Period: January - December 2021
Permit EPR/BJ7786IV |  |  |  | Operator: | Veolia ES Hampshire Ltd
Facility: | Integra North Energy Recovery Facility |  |  |  | Form: | S3/WU/1
Water Source |  | Usage (m3) | Specific Usage (m3/t) | Trends in Water Usage Year Parameter
[5 empty] | Named Water Source | Total Water Usage (m3) | Water per unit output
Mains Water |  | 25665 | 0.24487
Site Borehole |  | 0 | 0 | 2016 | Towns Water | 29635 | 0.3
River Abstraction |  | 0 | 0 | 2017 | Towns Water | 29635 | 0.31
|  |  |  | 2018 | Towns Water | 27443 | 0.29
|  |  |  | 2019 | Towns Water | 24730 | 0.25
TOTAL WATER USAGE |  | 25665 |  | 2020 | Towns Water | 24754 | 0.25
Operator's comments
Signed: |  |  |  |  | Date: | 24th January 2022

## S3PI1
Reporting of Performance Indicators for the Period: January - December 2021
Permit EPR/BJ7786IV |  |  |  |  | Operator: | Veolia ES Hampshire Ltd
Facility: | Integra North Energy Recovery Facility |  |  |  |  | Form: | S3/PI/1
| Total Municipal Waste Incinerated |  |  | 104811 |  | Tonnes
| Total Commercial Wastes Incinerated |  |  | 25843 |  | Tonnes
| Electrical Energy generated |  |  | 64430 |  | MWhrs
| Electrical Energy generated and exported |  |  | 55986 |  | MWhrs
| Electrical Energy generated and used on the installation |  |  | 8444 |  | MWhrs
Parameter |  | Average | Units |  | Trends in Environmental Performance Year Parameter
Supplementary Fuel Oil |  | 0.19176 | L/tonne of waste incinerated |  |  | Supplementary Fuel Oil Used |  | Waste Hazardous Score
Mass of Bottom Ash produced |  | 166.7478 | kg/tonne of waste incinerated |  | 2014 | 117,314 Litres |  | Awaiting Score Methodology
Mass of APC residues produced |  | 25.1596 | kg/tonne of waste incinerated |  | 2015 | 123,222 Litres |  | Awaiting Score Methodology
Mass of Carbon used |  | 0.1622 | kg/tonne of waste incinerated |  | 2016 | 82,723 Litres |  | Awaiting Score Methodology
Mass of Lime used |  | 7.5565 | kg/tonne of waste incinerated |  | 2017 | 74,380 Litres |  | Awaiting Score Methodology
Mass of Urea used |  | 1.5647 | kg/tonne of waste incinerated |  | 2018 | 92,410 Litres |  | Awaiting Score Methodology
Water use |  | 0.24487 | L/tonne of waste incinerated |  | 2019 | 53,589 Litres |  | Awaiting Score Methodology
Electrical energy imported and used at the installation |  | 80.5641 | KWhrs/tonne of waste incinerated |  | 2020 | 103,202 Litres |  | Awaiting Score Methodology
Operator's comments
Signed: | [5 empty] | Date: | 24th January 2022

## Air A8
Six-monthly Reporting of Emissions to Air for the period: July to December 2021
Permit EPR/BJ7786IV |  |  |  |  | Operator: | Veolia ES Hampshire Ltd
Facility: | Integra North Energy Recovery Facility |  |  |  |  | Form: | BJ7786IV/A8
Emission Point | Substance / Parameter | Emission Limit Value | Result [1] | Test Method [2] | Sample Date and Times [3] | Accreditation/ Certification [4] | Uncertainty [5]
A1 | Hydrogen fluoride | 2 mg/m3 over minimum 1 hour period | <0.044 | BS ISO 15713 | 10.08.2021 16:00-18:00 | UKAS+MCERTS | 0.0034
A1 | Cadmium & thallium and their compounds (total) | 0.5 mg/m3 over minimum 30 minute, maximum 8 hour period | 0.0011 | BS EN 14385 | 13.10.2021 10:04-11:07 | UKAS+MCERTS | 0.00018
A1 | Mercury and its compounds | 0.05 mg/m3 over minimum 30 minute, maximum 8 hour period | 0.0025 | BS EN 13211 | 13.10.2021 10:04-11:07 | UKAS+MCERTS | 0.001
A1 | Sb, As, Pb, Cr, Co, Cu, Mn, Ni and V and their compounds (total) | 0.5 mg/m3 over minimum 30 minute, maximum 8 hour period | 0.12 | BS EN 14385 | 13.10.2021 10:04-11:07 | UKAS+MCERTS | 0.023
A1 | Nitrous oxide (N2O) | No limit applies over minimum 1 hour period | 13.7 | BS EN ISO 21258 | 10.08.2021 16:00-18:00 | UKAS+MCERTS | 4
A1 | Dioxins / furans (I-TEQ)6 | 0.1 ng/m3 over minimum 6 hour, maximum 8 hour period | 0.0031-0.0033 | BS EN 1948-1,2,3 | 13.10.2021 11:39-17:44 | UKAS+MCERTS | 0.0006-0.0007
A1 | Dioxins / furans (WHO-TEQ Humans / Mammals) 6 | No limit applies, over minimum 6 hour 8 hour period | 0.0027-0.0030 | BS EN 1948-1,2,3 | 13.10.2021 11:39-17:44 | UKAS+MCERTS | 0.006
A1 | Dioxins / furans (WHO-TEQ Fish) 6 | No limit applies, over minimum 6 hour 8 hour period | 0.0025-0.0028 | BS EN 1948-1,2,3 | 13.10.2021 11:39-17:44 | UKAS+MCERTS | 0.0005-0.0006
A1 | Dioxins / furans (WHO-TEQ Birds) 6 | No limit applies, over minimum 6 hour 8 hour period | 0.0036-0.0039 | BS EN 1948-1,2,3 | 13.10.2021 11:39-17:44 | UKAS+MCERTS | 0.0007-0.0008
A1 | Dioxin-like PCBs (WHO-TEQ Humans / Mammals)6 | No limit applies, over minimum 6 hour 8 hour period | 0.00013 | BS EN 1948-4 | 13.10.2021 11:39-17:44 | UKAS+MCERTS | 2.8e-05
A1 | Dioxin-like PCBs (WHO-TEQ Fish)6 | No limit applies, over minimum 6 hour 8 hour period | 6.7e-06 | BS EN 1948-4 | 13.10.2021 11:39-17:44 | UKAS+MCERTS | 1e-06
A1 | Dioxin-like PCBs (WHO-TEQ Birds)6 | No limit applies, over minimum 6 hour 8 hour period | 0.00042 | BS EN 1948-4 | 13.10.2021 11:39-17:44 | UKAS+MCERTS | 8.7e-05
A1 | Poly-cyclic aromatic hydrocarbons (PAHs) Total | No limit applies, over minimum 6 hour 8 hour period | 0.89 | BS ISO 11338-1,2 | 12.10.2021 12:10-18:14 | UKAS+MCERTS | 0.18
A1 | Anthanthrene | No limit applies, over minimum 6 hour 8 hour period | <0.0013 | BS ISO 11338-1,2 | 12.10.2021 12:10-18:14 | UKAS+MCERTS | 0.00026
A1 | Benzo{a}anthracene | No limit applies, over minimum 6 hour 8 hour period | 0.0014 | BS ISO 11338-1,2 | 12.10.2021 12:10-18:14 | UKAS+MCERTS | 0.00029
A1 | Benzo[a]pyrene | No limit applies, over minimum 6 hour 8 hour period | <0.0013 | BS ISO 11338-1,2 | 12.10.2021 12:10-18:14 | UKAS+MCERTS | 0.00026
A1 | Benzo[b]fluoranthene | No limit applies, over minimum 6 hour 8 hour period | 0.0064 | BS ISO 11338-1,2 | 12.10.2021 12:10-18:14 | UKAS+MCERTS | 0.00133
A1 | Benzo[b]naph(2,1-d}thiophene | No limit applies, over minimum 6 hour 8 hour period | <0.0013 | BS ISO 11338-1,2 | 12.10.2021 12:10-18:14 | UKAS+MCERTS | 0.00026
A1 | Benzo[c]phenanthrene | No limit applies, over minimum 6 hour 8 hour period | <0.0013 | BS ISO 11338-1,2 | 12.10.2021 12:10-18:14 | UKAS+MCERTS | 0.00026
A1 | Benzo[ghi]perylene | No limit applies, over minimum 6 hour 8 hour period | 0.0022 | BS ISO 11338-1,2 | 12.10.2021 12:10-18:14 | UKAS+MCERTS | 0.00045
A1 | Benzo[k]fluoranthene | No limit applies, over minimum 6 hour 8 hour period | 0.0025 | BS ISO 11338-1,2 | 12.10.2021 12:10-18:14 | UKAS+MCERTS | 0.00052
A1 | Cholanthrene | No limit applies, over minimum 6 hour 8 hour period | <0.0013 | BS ISO 11338-1,2 | 12.10.2021 12:10-18:14 | UKAS+MCERTS | 0.00026
A1 | Chrysene | No limit applies, over minimum 6 hour 8 hour period | 0.0031 | BS ISO 11338-1,2 | 12.10.2021 12:10-18:14 | UKAS+MCERTS | 0.00064
A1 | Cyclopenta(c,d)pyrene | No limit applies, over minimum 6 hour 8 hour period | <0.0013 | BS ISO 11338-1,2 | 12.10.2021 12:10-18:14 | UKAS+MCERTS | 0.00026
A1 | Dibenzo[a,i]pyrene | No limit applies, over minimum 6 hour 8 hour period | <0.0013 | BS ISO 11338-1,2 | 12.10.2021 12:10-18:14 | UKAS+MCERTS | 0.00026
A1 | Dibenzo[ah]anthracene | No limit applies, over minimum 6 hour 8 hour period | <0.0013 | BS ISO 11338-1,2 | 12.10.2021 12:10-18:14 | UKAS+MCERTS | 0.00026
A1 | Fluoanthene | No limit applies, over minimum 6 hour 8 hour period | 0.018 | BS ISO 11338-1,2 | 12.10.2021 12:10-18:14 | UKAS+MCERTS | 0.00369
A1 | Indo[1,2,3-cd]pyrene | No limit applies, over minimum 6 hour 8 hour period | 0.0018 | BS ISO 11338-1,2 | 12.10.2021 12:10-18:14 | UKAS+MCERTS | 0.00038
A1 | Naphthalene | No limit applies, over minimum 6 hour 8 hour period | 0.84 | BS ISO 11338-1,2 | 12.10.2021 12:10-18:14 | UKAS+MCERTS | 0.17
[1] The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.
[2] Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with the Agency is used, then the appropriate identifier is given. In other cases the principal technique is stated, e.g. gas chromatography.
[3] For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements the percentage of the process operating time covered by the result is given.
[4] The accreditation status of the equipment and/or the monitoring organisation, as appropriate, for the methods used for both sampling and analysis.
[5] The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated.
[6] The result to be reported as a range based on: All congeners less than the detection limit assumed to be zero as a minimum, and all congeners less than the detection limit assumed to be at the detection limit as a maximum
Signed: | [5 empty] | 24th January 2022

## Permit Compliance
Annual Performance Report 2021 |  |  | Integra North Energy Recovery Facility
Summary of Permit Compliance
Compliance with permit limits for continuously monitored pollutants
The plant met its emission limits as shown in the table below:
Substance |  | Percentage time compliant during operation |  |  |  | Notes:
|  | Half-hourly limit |  | Daily limit |  | Report to 2 decimal places, i.e. xx.xx% Please provide a brief summary of each notification or non-compliance in the table (rather than just referring to notifications that were sent to the Regulator).
Particulates |  | 100% |  | 100%
Oxides of nitrogen |  | 100% |  | 100%
Sulphur dioxide |  | 100% |  | 100%
Carbon monoxide |  | 100.00 % 95% of 10-min averages |  | 100%
Total organic carbon |  | 100% |  | 100%
Hydrogen chloride |  | 100% |  | 100%
Summary of any notifications or non-compliances under the permit
Date | Summary of notification or non-compliance [including Line/Reference] |  | Reason |  | Measures taken to prevent reoccurrence
Summary of any complaints received and actions to taken to resolve them.
Date | Summary of complaint [including Line/Reference] |  | Reason * |  | Measures taken to prevent reoccurrence
* including whether substantiated by the operator or the EA

## Improvements
Annual Performance Report 2021 | Integra North Energy Recovery Facility
Summary of Plant Improvements
Summary of any efficiency improvements that have been completed within the year.
Continuous planned preventive maintenance strategy and streamlining of assets
Summary of any permit improvement conditions that have been completed within the year and the resulting environmental benefits.
All improvement conditions discharged
Summary of any changes to the plant or operating techniques which required a variation to the permit and a summary of the resulting environmental impact.
None
Summary of any other improvements made to the plant or planned to be made and a summary of the resulting environmental benefits.
Continuation of 24 month outage strategy resulting in higher availability and less waste diversion to Landfill Every practicable opportunity to use the heat rejected at the steam condensers for beneficial local use is investigated. To date no cost effective or practicable options have become available. The site will continue to identify all possible opportunities, and investigate the practicalities of its installation. All viable developments will be implemented at the earliest opportunity. Raw materials used on site are trended by the Facility Manager and recorded on the company intranet so that benchmarks are visible to the group. These Key Performance Indicators (KPIs) are reviewed daily, weekly, monthly and annually. If any opportunities arise which would result in reduction or avoidance in raw material usage, they will be implemented at the earliest convenience. There are no improvements to be made at this time regarding the use of raw materials at the site.

## Public Liasion
Annual Performance Report 2021 |  | Integra North Energy Recovery Facility
Details of Public & Stakeholder Liaison
Summary of events held during the reporting year.
Date | Description
Suspended due to COVID-19 | Veolia Wonder Day: Veolia invites visitors from across the county to come along and discover what happens at our waste management facilities. Behind the scenes tours and activities offer an insight into the entire integrated network of our recycling and recovery operations and the importance of disposing of your waste responsibly.
List of events planned for next year
Date | Description
TBC | Veolia Wonder Day: Veolia invites visitors from across the county to come along and discover what happens at our waste management facilities. Behind the scenes tours and activities offer an insight into the entire integrated network of our recycling and recovery operations and the importance of disposing of your waste responsibly.
If you wish to be involved in the public liaison programme, please contact _________________

## Residue Quality
Annual Performance Report 2021 |  |  | Integra North Energy Recovery Facility
Residue Quality Monitoring Requirements
Summary of monitoring undertaken and compliance
IBA - Two samples per month are analysed under the ESA protocol One sample per quarter analysed for Permit requirements
APCr - One sample per quarter analysed for Permit requirements
Commentary on any specific events
Date & Event | Description
Residue Quality Monitoring Results
Parameter (unit) | Limit | Normal Operation
|  | Bottom ash |  | APC Residues
Loss on Ignition (average %) | <5%
Total Organic Carbon (average %) | <3% | 1.4
No. of Assessments Undertaken | --- | 4 |  | 4
No. of Hazardous Results | --- | 0
Comments :
TOC result is average of quarterly values

## Water
Annual Performance Report 2021 |  |  | Integra North Energy Recovery Facility
Emissions to Water
Summary of monitoring undertaken and compliance
3 discharges to Sewer in 2021, samples were taken on all occasions and analysed in accordance with the Permit
Commentary on any specific events
Date & Event | Description
Emissions to Water / Sewer
Parameter |  | Monitoring Frequency |  | Limit | Target | Max. | Average
Mercury |  | upon batch discharge |  | 0.03 mg/l | <0.03 | <0.01 | <0.01
Cadmium |  | upon batch discharge |  | 0.05 mg/l | <0.05 | <0.01 | <0.01

## Air (periodic)
Annual Performance Report 2021 |  |  | Integra North Energy Recovery Facility
Emissions to Air (periodically monitored)
Summary of monitoring undertaken, standards used and compliance | [8 empty] | Notes:
Monitoring undertaken in accordance with the standards listed in the Permit, compliance was maintained for 100% of 2021 | [8 empty] | Template may require adjustment for any bespoke monitoring requirements of permit.
Results of emissions to air that are periodically monitored
Substance | Ref. Period | Emission Limit Value |  | Average |  |  |  |  | User to add additional tables as necessary, depending on whether quarterly or bi-annual reporting is required for the compliance year
|  |  |  | A1 | A2 | A3 | A4 | A5
Hydrogen fluoride | 1 hr | 2 mg/m3 |  | 0.046
Cd and Th and their compounds | 6-8hrs | 0.05 mg/m3 |  | 0.00589
Hg and its compounds | 6-8hrs | 0.05 mg/m3 |  | 0.00185
Sb, As, Pb, Cr, Co, Cu, Mn, Ni, V and their compounds | 6-8hrs | 0.5 mg/m3 |  | 0.077
Dioxins & Furans (I-TEQ) | 6-8hrs | 0.1 ng/m3 |  | 0.0068
Dioxins & Furans (WHO-TEQ Humans / Mammals) | 6-8hrs | None set ng/m3 |  | 0.0061
Dioxins & Furans (WHO-TEQ Fish) | 6-8hrs | None set ng/m3 |  | 0.001825
Dioxins & Furans (WHO-TEQ Birds) | 6-8hrs | None set ng/m3 |  | 0.0111
PCBs (WHO-TEQ Humans / Mammals) | 6-8hrs | None set ng/m3 |  | 0.00038
PCBs (WHO-TEQ Fish) | 6-8hrs | None set ng/m3 |  | 1.835e-05
PCBs (WHO-TEQ Birds) | 6-8hrs | None set ng/m3 |  | 0.000705
Anthanthrene | 6-8hrs | None set µg/m3 |  | 0.001
Benzo(a)anthracene | 6-8hrs | None set µg/m3 |  | 0.00165
Benzo(a)pyrene | 6-8hrs | None set µg/m3 |  | 0.001
Benzo(b)fluoranthene | 6-8hrs | None set µg/m3 |  | 0.0095
Benzo(b)naptho(2,1-d) thiophene | 6-8hrs | None set µg/m3 |  | 0.001
Benzo(c)phenanthrene | 6-8hrs | None set µg/m3 |  | 0.001
Benzo(ghi)perylene | 6-8hrs | None set µg/m3 |  | 0.0104
Benzo(k)fluoranthene | 6-8hrs | None set µg/m3 |  | 0.0016
Cholanthrene | 6-8hrs | None set µg/m3 |  | 0.001
Chrysene | 6-8hrs | None set µg/m3 |  | 0.0036
Cyclopenta(cd)pyrene | 6-8hrs | None set µg/m3 |  | 0.0033
Dibenzo(ai)pyrene | 6-8hrs | None set µg/m3 |  | 0.001
Dibenzo(ah)anthracene | 6-8hrs | None set µg/m3 |  | 0.001
Fluoranthene | 6-8hrs | None set µg/m3 |  | 0.010435
Indeno(123-cd) pyrene | 6-8hrs | None set µg/m3 |  | 0.00765
Naphthalene | 6-8hrs | None set µg/m3 |  | 0.4998
Comments :
< LOD as reported as LOD

## Air (CEMS)
Annual Performance Report 2021 | [7 empty] | Integra North Energy Recovery Facility
Emissions to Air (continuously monitored)
Notes:
Summary of monitoring undertaken, standards used and compliance | [12 empty] | Template may require adjustment for any bespoke monitoring requirements of permit
Monitoring undertaken in accordance with the standards listed in the Permit, compliance was maintained for 100% of 2021 | [12 empty] | Report to 2 decimal places, i.e. xx.xx%
Results of emissions to air that are continuously monitored (maximum and average values for each line)
Substance | Reference Period | Emission Limit Value | A1 |  | A2 |  | A3 |  | A4 |  | A5
|  |  | Max. | Avg. | Max. | Avg. | Max. | Avg. | Max. | Avg. | Max. | Avg.
Oxides of nitrogen | Daily mean | 200 mg/m3 | 186.49 | 169.7367
| ½ hourly mean | 400 mg/m3 | 346.24 | 169.9167
Particulates | Daily mean | 10 mg/m3 | 2.78 | 0.93417
| ½ hourly mean | 30 mg/m3 | 12.33 | 0.93583
Total Organic Carbon | Daily mean | 10 mg/m3 | 1.14 | 0.19917
| ½ hourly mean | 20 mg/m3 | 11.14 | 0.2025
Hydrogen chloride | Daily mean | 10 mg/m3 | 7.77 | 5.6725
| ½ hourly mean | 60 mg/m3 | 38.3 | 5.6733
Sulphur dioxide | Daily mean | 50 mg/m3 | 24.3 | 17.1583
| ½ hourly mean | 200 mg/m3 | 73.96 | 17.1117
Carbon monoxide | Daily mean | 50 mg/m3 | 33.15 | 7.0767
| 95%ile 10-min avg * | 150 mg/m3 * | 1207.43 | 7.1358
Ammonia | Daily mean | No limit set | 5.2508 | 5.2483
* = delete or amend as appropriate
Comments :

## HCl
Annual Performance Report 2021 |  |  |  | Integra North Energy Recovery Facility
Monitoring of Hydrogen Chloride emissions |  |  | Whole Installation |  |  | See Notes in Cell Q3 | Monitoring of Hydrogen Chloride emissions |  |  |  | Per Combustion Line |  | Notes:
User to add logic to complete Whole installation, Table A5:G18. From the data in Per Combustion Line, Table J6:O79, subject to No. of lines installed
mg/Nm3 | 1/2 Hourly Reference Periods |  |  | Daily Reference Periods
2021 | 1/2 hourly HCl ELV | Monthly 1/2 hourly mean | Highest 1/2 hourly maximum | Daily HCl ELV | Monthly daily mean | Highest daily maximum | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
Jan | 60 | 5.84 | 29.3 | 10 | 5.84 | 7.77 | A1 | Jan | 5.84 | 29.3 | 5.84 | 7.77
Feb | 60 | 5.35 | 23.26 | 10 | 5.35 | 7.65 |  | Feb | 5.35 | 23.26 | 5.35 | 7.65
Mar | 60 | 5.36 | 27.18 | 10 | 5.36 | 6.85 |  | Mar | 5.36 | 27.18 | 5.36 | 6.85 | Whole Installation table A5:G18:
Apr | 60 | 4.98 | 38.3 | 10 | 4.98 | 7.39 |  | Apr | 4.98 | 38.3 | 4.98 | 7.39 | Mean: for 1/2 hourly and daily periods calculate mean of values across all operational combustion lines for the month
May | 60 | 5.73 | 35.22 | 10 | 5.73 | 6.74 |  | May | 5.73 | 35.22 | 5.73 | 6.74
Jun | 60 | 5.91 | 20.83 | 10 | 5.91 | 6.77 |  | Jun | 5.91 | 20.83 | 5.91 | 6.77
Jul | 60 | 5.76 | 30.58 | 10 | 5.75 | 7.07 |  | Jul | 5.76 | 30.58 | 5.75 | 7.07 | Maximum: for 1/2 hourly and daily periods use the highest value across all operational combustion lines for the month
Aug | 60 | 6.14 | 20.98 | 10 | 6.14 | 6.93 |  | Aug | 6.14 | 20.98 | 6.14 | 6.93
Sep | 60 | 6.16 | 15.81 | 10 | 6.16 | 6.97 |  | Sep | 6.16 | 15.81 | 6.16 | 6.97
Oct | 60 | 5.19 | 24.84 | 10 | 5.21 | 7.34 |  | Oct | 5.19 | 24.84 | 5.21 | 7.34
Nov | 60 | 6.31 | 10.27 | 10 | 6.32 | 6.38 |  | Nov | 6.31 | 10.27 | 6.32 | 6.38
Dec | 60 | 5.35 | 30.5 | 10 | 5.32 | 7.06 |  | Dec | 5.35 | 30.5 | 5.32 | 7.06
[8 empty] | Annual | 5.6733 | 38.3 | 5.6725 | 7.77
[7 empty] | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A2 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A3 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Comments : | [7 empty] | Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A4 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A5 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0

## SO2
Annual Performance Report 2021 |  |  |  | Integra North Energy Recovery Facility
Monitoring of Sulphur dioxide emissions |  |  | Whole Installation |  |  | See Notes in Cell Q3 | Monitoring of Sulphur dioxide emissions |  |  |  | Per Combustion Line |  | Notes:
User to add logic to complete Whole installation, Table A5:G18. From the data in Per Combustion Line, Table J6:O79, subject to No. of lines installed
mg/Nm3 | 1/2 Hourly Reference Periods |  |  | Daily Reference Periods
2021 | 1/2 hourly SO2 ELV | Monthly 1/2 hourly mean | Highest 1/2 hourly maximum | Daily SO2 ELV | Monthly daily mean | Highest daily maximum | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
Jan | 200 | 18.47 | 39.6 | 50 | 18.47 | 21.45 | A1 | Jan | 18.47 | 39.6 | 18.47 | 21.45
Feb | 200 | 19.22 | 40.26 | 50 | 19.22 | 22.38 |  | Feb | 19.22 | 40.26 | 19.22 | 22.38
Mar | 200 | 21.59 | 73.96 | 50 | 21.58 | 24.3 |  | Mar | 21.59 | 73.96 | 21.58 | 24.3 | Whole Installation table A5:G18:
Apr | 200 | 18.12 | 66.72 | 50 | 18.13 | 23.62 |  | Apr | 18.12 | 66.72 | 18.13 | 23.62 | Mean: for 1/2 hourly and daily periods calculate mean of values across all operational combustion lines for the month
May | 200 | 19.81 | 64.28 | 50 | 19.81 | 23.43 |  | May | 19.81 | 64.28 | 19.81 | 23.43
Jun | 200 | 17.44 | 42.95 | 50 | 17.44 | 19.69 |  | Jun | 17.44 | 42.95 | 17.44 | 19.69
Jul | 200 | 17.28 | 42.37 | 50 | 17.27 | 19.61 |  | Jul | 17.28 | 42.37 | 17.27 | 19.61 | Maximum: for 1/2 hourly and daily periods use the highest value across all operational combustion lines for the month
Aug | 200 | 15.5 | 38.26 | 50 | 15.5 | 18.82 |  | Aug | 15.5 | 38.26 | 15.5 | 18.82
Sep | 200 | 14.77 | 31.18 | 50 | 14.77 | 16.79 |  | Sep | 14.77 | 31.18 | 14.77 | 16.79
Oct | 200 | 14.42 | 45.07 | 50 | 14.46 | 20.8 |  | Oct | 14.42 | 45.07 | 14.46 | 20.8
Nov | 200 | 15.69 | 22.69 | 50 | 16.27 | 17.41 |  | Nov | 15.69 | 22.69 | 16.27 | 17.41
Dec | 200 | 13.03 | 50.98 | 50 | 12.98 | 17.07 |  | Dec | 13.03 | 50.98 | 12.98 | 17.07
[8 empty] | Annual | 17.1117 | 73.96 | 17.1583 | 24.3
[7 empty] | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A2 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A3 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Comments : | [7 empty] | Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A4 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A5 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0

## NOx
Annual Performance Report 2021 |  |  |  | Integra North Energy Recovery Facility
Monitoring of Oxides of Nitrogen emissions |  |  | Whole Installation |  |  | See Notes in Cell Q3 | Monitoring of Oxides of Nitrogen emissions |  |  |  | Per Combustion Line |  | Notes:
User to add logic to complete Whole installation, Table A5:G18. From the data in Per Combustion Line, Table J6:O79, subject to No. of lines installed
mg/Nm3 | 1/2 Hourly Reference Periods |  |  | Daily Reference Periods
2021 | 1/2 hourly NOx ELV | Monthly 1/2 hourly mean | Highest 1/2 hourly maximum | Daily NOx ELV | Monthly daily mean | Highest daily maximum | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
Jan | 400 | 173.57 | 233.69 | 200 | 173.57 | 185.19 | A1 | Jan | 173.57 | 233.69 | 173.57 | 185.19
Feb | 400 | 176.45 | 260.45 | 200 | 176.45 | 186.49 |  | Feb | 176.45 | 260.45 | 176.45 | 186.49
Mar | 400 | 174.71 | 214.52 | 200 | 174.71 | 178.69 |  | Mar | 174.71 | 214.52 | 174.71 | 178.69 | Whole Installation table A5:G18:
Apr | 400 | 167.52 | 288.53 | 200 | 167.55 | 178.65 |  | Apr | 167.52 | 288.53 | 167.55 | 178.65 | Mean: for 1/2 hourly and daily periods calculate mean of values across all operational combustion lines for the month
May | 400 | 174.08 | 212.29 | 200 | 174.09 | 181.95 |  | May | 174.08 | 212.29 | 174.09 | 181.95
Jun | 400 | 170.27 | 346.24 | 200 | 170.28 | 182.46 |  | Jun | 170.27 | 346.24 | 170.28 | 182.46
Jul | 400 | 164.03 | 202.92 | 200 | 164.01 | 181.37 |  | Jul | 164.03 | 202.92 | 164.01 | 181.37 | Maximum: for 1/2 hourly and daily periods use the highest value across all operational combustion lines for the month
Aug | 400 | 169.61 | 209.12 | 200 | 169.56 | 179.25 |  | Aug | 169.61 | 209.12 | 169.56 | 179.25
Sep | 400 | 166.99 | 257.75 | 200 | 166.98 | 179.33 |  | Sep | 166.99 | 257.75 | 166.98 | 179.33
Oct | 400 | 168.68 | 225.34 | 200 | 168.7 | 180.12 |  | Oct | 168.68 | 225.34 | 168.7 | 180.12
Nov | 400 | 162.15 | 188.57 | 200 | 159.69 | 162.2 |  | Nov | 162.15 | 188.57 | 159.69 | 162.2
Dec | 400 | 170.94 | 242.42 | 200 | 171.25 | 182.91 |  | Dec | 170.94 | 242.42 | 171.25 | 182.91
[8 empty] | Annual | 169.9167 | 346.24 | 169.7367 | 186.49
[7 empty] | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A2 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A3 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Comments : | [7 empty] | Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A4 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A5 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0

## TOC
Annual Performance Report 2021 |  |  |  | Integra North Energy Recovery Facility
Monitoring of Total organic carbon emissions |  |  | Whole Installation |  |  | See Notes in Cell Q3 | Monitoring of Total organic carbon emissions |  |  |  | Per Combustion Line |  | Notes:
User to add logic to complete Whole installation, Table A5:G18. From the data in Per Combustion Line, Table J6:O79, subject to No. of lines installed
mg/Nm3 | 1/2 Hourly Reference Periods |  |  | Daily Reference Periods
2021 | 1/2 hourly TOC ELV | Monthly 1/2 hourly mean | Highest 1/2 hourly maximum | Daily TOC ELV | Monthly daily mean | Highest daily maximum | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
Jan | 20 | 0.45 | 6.08 | 10 | 0.45 | 1.14 | A1 | Jan | 0.45 | 6.08 | 0.45 | 1.14
Feb | 20 | 0.33 | 6.05 | 10 | 0.33 | 0.62 |  | Feb | 0.33 | 6.05 | 0.33 | 0.62
Mar | 20 | 0.2 | 5.27 | 10 | 0.19 | 0.59 |  | Mar | 0.2 | 5.27 | 0.19 | 0.59 | Whole Installation table A5:G18:
Apr | 20 | 0.28 | 10.73 | 10 | 0.28 | 0.69 |  | Apr | 0.28 | 10.73 | 0.28 | 0.69 | Mean: for 1/2 hourly and daily periods calculate mean of values across all operational combustion lines for the month
May | 20 | 0.24 | 3.2 | 10 | 0.24 | 0.59 |  | May | 0.24 | 3.2 | 0.24 | 0.59
Jun | 20 | 0.16 | 6.05 | 10 | 0.16 | 0.28 |  | Jun | 0.16 | 6.05 | 0.16 | 0.28
Jul | 20 | 0.15 | 3.55 | 10 | 0.15 | 0.66 |  | Jul | 0.15 | 3.55 | 0.15 | 0.66 | Maximum: for 1/2 hourly and daily periods use the highest value across all operational combustion lines for the month
Aug | 20 | 0.14 | 6.6 | 10 | 0.14 | 0.29 |  | Aug | 0.14 | 6.6 | 0.14 | 0.29
Sep | 20 | 0.14 | 3.07 | 10 | 0.14 | 0.61 |  | Sep | 0.14 | 3.07 | 0.14 | 0.61
Oct | 20 | 0.12 | 11.14 | 10 | 0.12 | 0.7 |  | Oct | 0.12 | 11.14 | 0.12 | 0.7
Nov | 20 | 0.1 | 6.15 | 10 | 0.07 | 0.08 |  | Nov | 0.1 | 6.15 | 0.07 | 0.08
Dec | 20 | 0.12 | 3.91 | 10 | 0.12 | 0.54 |  | Dec | 0.12 | 3.91 | 0.12 | 0.54
[8 empty] | Annual | 0.2025 | 11.14 | 0.19917 | 1.14
[7 empty] | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A2 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A3 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Comments : | [7 empty] | Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A4 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A5 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0

## Particulates
Annual Performance Report 2021 |  |  |  | Integra North Energy Recovery Facility
Monitoring of Particulate matter emissions |  |  | Whole Installation |  |  | See Notes in Cell Q3 | Monitoring of Particulate matter emissions |  |  |  | Per Combustion Line |  | Notes:
User to add logic to complete Whole installation, Table A5:G18. From the data in Per Combustion Line, Table J6:O79, subject to No. of lines installed
mg/Nm3 | 1/2 Hourly Reference Periods |  |  | Daily Reference Periods
2021 | 1/2 hourly PM ELV | Monthly 1/2 hourly mean | Highest 1/2 hourly maximum | Daily PM ELV | Monthly daily mean | Highest daily maximum | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
Jan | 30 | 1.42 | 3.44 | 10 | 1.42 | 2.78 | A1 | Jan | 1.42 | 3.44 | 1.42 | 2.78
Feb | 30 | 1.06 | 12.33 | 10 | 1.06 | 2.1 |  | Feb | 1.06 | 12.33 | 1.06 | 2.1
Mar | 30 | 0.62 | 1.04 | 10 | 0.62 | 0.86 |  | Mar | 0.62 | 1.04 | 0.62 | 0.86 | Whole Installation table A5:G18:
Apr | 30 | 0.53 | 4.02 | 10 | 0.53 | 0.65 |  | Apr | 0.53 | 4.02 | 0.53 | 0.65 | Mean: for 1/2 hourly and daily periods calculate mean of values across all operational combustion lines for the month
May | 30 | 0.61 | 0.85 | 10 | 0.61 | 0.73 |  | May | 0.61 | 0.85 | 0.61 | 0.73
Jun | 30 | 0.58 | 3.59 | 10 | 0.58 | 0.66 |  | Jun | 0.58 | 3.59 | 0.58 | 0.66
Jul | 30 | 0.7 | 1.36 | 10 | 0.7 | 0.82 |  | Jul | 0.7 | 1.36 | 0.7 | 0.82 | Maximum: for 1/2 hourly and daily periods use the highest value across all operational combustion lines for the month
Aug | 30 | 0.85 | 2.79 | 10 | 0.85 | 0.99 |  | Aug | 0.85 | 2.79 | 0.85 | 0.99
Sep | 30 | 0.99 | 1.5 | 10 | 0.99 | 1.13 |  | Sep | 0.99 | 1.5 | 0.99 | 1.13
Oct | 30 | 1.29 | 7.48 | 10 | 1.3 | 2.49 |  | Oct | 1.29 | 7.48 | 1.3 | 2.49
Nov | 30 | 1.24 | 1.92 | 10 | 1.21 | 1.3 |  | Nov | 1.24 | 1.92 | 1.21 | 1.3
Dec | 30 | 1.34 | 3.56 | 10 | 1.34 | 1.75 |  | Dec | 1.34 | 3.56 | 1.34 | 1.75
[8 empty] | Annual | 0.93583 | 12.33 | 0.93417 | 2.78
[7 empty] | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A2 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A3 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Comments : | [7 empty] | Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A4 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A5 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0

## CO 95% 10 min
Annual Performance Report 2021 |  |  |  | Integra North Energy Recovery Facility
Monitoring of Carbon Monoxide (10-minute avg) |  |  |  | Whole Installation |  |  | See Notes in Cell S3 | Monitoring of Carbon Monoxide (10-minute avg) |  |  |  |  | Per Combustion Line |  | Notes: | Notes:
User to add logic to complete Whole installation, Table A5:H18. From the data in Per Combustion Line, Table K6:Q79, subject to No. of lines installed
mg/Nm3 | 10-minute Reference Periods |  |  |  | Daily Reference Periods
2021 | 95%ile 10-min avg CO ELV | 95%ile 10-min avg maximum | Monthly CO 10-min avg mean | 10-min avg maximum | Daily CO ELV | Monthly daily mean | Highest daily maximum |  | 2021 | mg/Nm3 | 95%ile 10-min avg maximum | Monthly CO 10-min avg mean | 10-min avg maximum | Monthly daily mean | Monthly daily maximum
Jan | 150 | 13.1 | 5.25 | 558.77 | 50 | 5.25 | 8.4 |  | A1 | Jan | 13.1 | 5.25 | 558.77 | 5.25 | 8.4
Feb | 150 | 10.97 | 5.39 | 629.95 | 50 | 5.39 | 10.05 |  |  | Feb | 10.97 | 5.39 | 629.95 | 5.39 | 10.05
Mar | 150 | 12.68 | 5.03 | 374.51 | 50 | 5.03 | 8.62 |  |  | Mar | 12.68 | 5.03 | 374.51 | 5.03 | 8.62 | Whole Installation table A5:H18:
Apr | 150 | 11.23 | 4.54 | 567.56 | 50 | 4.55 | 9.59 |  |  | Apr | 11.23 | 4.54 | 567.56 | 4.55 | 9.59 | Mean: for 10-min and daily periods use average of all operational combustion lines.
May | 150 | 91.44 | 8.05 | 356.71 | 50 | 8.06 | 33.15 |  |  | May | 91.44 | 8.05 | 356.71 | 8.06 | 33.15
Jun | 150 | 12.55 | 6.23 | 527.76 | 50 | 6.23 | 10.17 |  |  | Jun | 12.55 | 6.23 | 527.76 | 6.23 | 10.17
Jul | 150 | 16.87 | 7.69 | 394.52 | 50 | 7.7 | 12.41 |  |  | Jul | 16.87 | 7.69 | 394.52 | 7.7 | 12.41 | Maximum: for 10-min and daily periods use the highest of all operational combustion lines in any month.
Aug | 150 | 13.89 | 7.44 | 515.52 | 50 | 7.44 | 10.69 |  |  | Aug | 13.89 | 7.44 | 515.52 | 7.44 | 10.69
Sep | 150 | 15.44 | 5.3 | 591.21 | 50 | 5.3 | 9.25 |  |  | Sep | 15.44 | 5.3 | 591.21 | 5.3 | 9.25
Oct | 150 | 49.96 | 9.26 | 1207.43 | 50 | 9.24 | 20.16 |  |  | Oct | 49.96 | 9.26 | 1207.43 | 9.24 | 20.16
Nov | 150 | 18.61 | 13.56 | 441.45 | 50 | 13.03 | 15.35 |  |  | Nov | 18.61 | 13.56 | 441.45 | 13.03 | 15.35
Dec | 150 | 20.32 | 7.89 | 839.41 | 50 | 7.7 | 14.01 |  |  | Dec | 20.32 | 7.89 | 839.41 | 7.7 | 14.01
[10 empty] | Annual | 23.9217 | 7.1358 | 1207.43 | 7.0767 | 33.15
[9 empty] | 2021 | mg/Nm3 | 95%ile 10-min avg maximum | Monthly CO 10-min avg mean | 10-min avg maximum | Monthly daily mean | Monthly daily maximum
[9 empty] | A2 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[10 empty] | Annual | #DIV/0! |  | 0 | #DIV/0! | 0
[9 empty] | 2021 | mg/Nm3 | 95%ile 10-min avg maximum | Monthly CO 10-min avg mean | 10-min avg maximum | Monthly daily mean | Monthly daily maximum
[9 empty] | A3 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Comments : | [9 empty] | Dec
Environment Agency explanatory note: The 10-minute average ELV is based on the “95th percentile”. In this case this means that 95% of the 10 minute averages in the relevant 24-hour period (i.e. 137) must be below 150 mg/Nm3, and 5% (i.e. 7) are allowed to be any value above 150 mg/Nm3. Whilst we expect operators to minimise CO emissions at all times, it is perfectly acceptable for the value of the maximum 10-minute average to be above 150 mg/Nm3, provided the 95th percentile ELV has been met for that period. | [9 empty] | Annual | #DIV/0! |  | 0 | #DIV/0! | 0
[9 empty] | 2021 | mg/Nm3 | 95%ile 10-min avg maximum | Monthly CO 10-min avg mean | 10-min avg maximum | Monthly daily mean | Monthly daily maximum
[9 empty] | A4 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[10 empty] | Annual | #DIV/0! |  | 0 | #DIV/0! | 0
[9 empty] | 2021 | mg/Nm3 | 95%ile 10-min avg maximum | Monthly CO 10-min avg mean | 10-min avg maximum | Monthly daily mean | Monthly daily maximum
[9 empty] | A5 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[10 empty] | Annual | #DIV/0! |  | 0 | #DIV/0! | 0

## NH3
Annual Performance Report 2021 |  |  |  | Integra North Energy Recovery Facility
Monitoring of Ammonia emissions |  |  | Whole Installation |  |  | See Notes in Cell Q3 | Monitoring of Ammonia emissions |  |  |  | Per Combustion Line |  | Notes:
User to add logic to complete Whole installation, Table A5:G18. From the data in Per Combustion Line, Table J6:O79, subject to No. of lines installed
mg/Nm3 | 1/2 Hourly Reference Periods |  |  | Daily Reference Periods
2021 | 1/2 hourly NH3 ELV | Monthly 1/2 hourly mean | Highest 1/2 hourly maximum | Daily NH3 ELV | Monthly daily mean | Highest daily maximum | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
Jan | 0 | 5.91 | 12.46 | 10 | 5.91 | 7.03 | A1 | Jan | 5.91 | 12.46 | 5.91 | 7.03
Feb | 0 | 4.72 | 9.59 | 10 | 4.72 | 5.78 |  | Feb | 4.72 | 9.59 | 4.72 | 5.78
Mar | 0 | 5.33 | 12.15 | 10 | 5.33 | 8.26 |  | Mar | 5.33 | 12.15 | 5.33 | 8.26 | Whole Installation table A5:G18:
Apr | 0 | 4.2 | 11.24 | 10 | 4.2 | 6.83 |  | Apr | 4.2 | 11.24 | 4.2 | 6.83 | Mean: for 1/2 hourly and daily periods calculate mean of values across all operational combustion lines for the month
May | 0 | 5.92 | 16.02 | 10 | 5.92 | 7.94 |  | May | 5.92 | 16.02 | 5.92 | 7.94
Jun | 0 | 5.88 | 12.87 | 10 | 5.88 | 7.39 |  | Jun | 5.88 | 12.87 | 5.88 | 7.39
Jul | 0 | 5.95 | 11.63 | 10 | 5.95 | 7.57 |  | Jul | 5.95 | 11.63 | 5.95 | 7.57 | Maximum: for 1/2 hourly and daily periods use the highest value across all operational combustion lines for the month
Aug | 0 | 5.04 | 10.16 | 10 | 5.04 | 7.14 |  | Aug | 5.04 | 10.16 | 5.04 | 7.14
Sep | 0 | 4.91 | 10.32 | 10 | 4.91 | 6.42 |  | Sep | 4.91 | 10.32 | 4.91 | 6.42
Oct | 0 | 5.04 | 12.33 | 10 | 5.01 | 7.06 |  | Oct | 5.04 | 12.33 | 5.01 | 7.06
Nov | 0 | 5.61 | 12.56 | 10 | 5.69 | 5.95 |  | Nov | 5.61 | 12.56 | 5.69 | 5.95
Dec | 0 | 4.47 | 11.4 | 10 | 4.45 | 6.13 |  | Dec | 4.47 | 11.4 | 4.45 | 6.13
[8 empty] | Annual | 5.2483 | 16.02 | 5.2508 | 8.26
[7 empty] | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A2 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A3 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Comments : | [7 empty] | Dec
An indicated ELV value of zero in the table above means that no ammonia limit is set in the permit. | [7 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A4 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2021 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A5 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0