The Environmental Permitting (England and Wales) Regulations 2010

Permit: EPR/LP3030XA Cardiff Energy Recovery Facility

Annual Performance Report 2017

Prepared by: Viridor, Trident Park ERF, Glass Avenue, Cardiff. CF24 5EN

Version: 1.0 Issue Date: 25/04/2018

Quality Assurance

This report has been prepared with all reasonable skill, care and diligence. Information reported herein is based on the interpretation of data collected and has been accepted in good faith as being accurate and valid.

|  | Report Details |  |  |
| --- | --- | --- | --- |
|  | Report Title: | Cardiff Energy Recovery Facility - Annual Performance Report 2017 |  |
|  | Report Date: | 25/01/2018 |  |
|  | Version: | 1 |  |
|  | Report Generated By |  |  |
|  | Name: | Muriel Alix |  |
|  | Position: | Data Analyst |  |
|  | Report Approved By |  |  |
|  | Name: | Gwyn Jones |  |
|  | Position: | EHS Manager |  |

## 1. 	Introduction

Cardiff Energy Recovery Facility is located immediately north of Cardiff Docks. The facility will process approximately 22.96 tonnes of residual municipal and Commercial and Industrial (C&I) waste per line, per hour and has the capability of exporting approximately 30MW of electrical power.

In accordance with the requirements of Condition 4.2.2, Schedule 4 and Table S4.1 of Permit EPR/LP3030XA issued by Natural Resources Wales to Viridor Waste Management Limited (Viridor) initially on 4th November 2010, Viridor is required to produce an annual performance report which is to be submitted to Natural Resources Wales by the 30th April as agreed in writing with Natural Resources Wales of each year.

Viridor took over the operation of the Plant on 31st January 2015; therefore 2017 is the third year of operations at the ERF.

This report summarises the environmental and performance data collected at the site 1st January 2017 – 31st December 2017 and fulfils the reporting requirement of Chapter IV, Article 55 (2) of the Industrial Emissions Directive.

The report will cover the following areas of environmental monitoring:

Section 2 – Point Source Emissions to Air

Section 3 – Point Source Emissions to Water

Section 4 – Residue Quality Monitoring Requirements

Section 5 – Performance Parameters

# 2.	Point Source Emissions to Air

## 2.1.	Introduction

Permit Condition 3.5.1(a) and Tables S3.1 and S3.1(a) require Viridor to undertake performance monitoring of the point source emissions to air arising at sample points A1 and A2.

A summary of the point source emissions to air monitoring data at sample point A1 and A2 for the period is included as Table 1.

## 2.2	Commentary on Data

The recorded concentrations remained compliant with the limits set out in Permit Tables S3.1 and S3.1 (a) during the review period except for those listed in 2.3.

The “daily mean” max values for Carbon Monoxide (CO) spiked on several occasions during June and July 2017.  By undertaking a detailed review of operations and having discussions with suppliers the root cause of these CO spikes was attributed to wear and tear of triangular metal plates (referred to as ‘sharks teeth’) on the grate. As a result, these metal plates were grinded off and new ones welded back in their place. The NRW was informed of these CO spikes through appropriate communications. Since the new metal plates have been fitted to the grate no further CO spikes have been experienced. Planned preventative maintenance (i.e. timely replacement of the metal plates) is now in place to avoid a re-occurrence of the CO spikes.

Line 1 was in operation for 89.6% of the year and Line 2 for 88.7%.

Note 1: Detail of periodic sampling timings, uncertainty and method used have previously been supplied to Natural Resources Wales within the 2017 quarterly reports.

Note 2: Results recorded by both, periodic and continuous monitoring have broadly been within the range expected for the energy recovery operation, with exception to the exceedances included in 2.3 below.

## 2.3	Schedule Notices Issued

22 February 2017 _ Schedule 5 Notification was submitted due to elevated CO reading.

17 April 2017, 22 April 2017, 24 April 2017, 2 May 2017, 30 May 2017 _ Schedule 5 Notification was submitted due to elevated CO readings.

1 June 2017, 6 June 2017 Schedule 5 Notification was submitted for an abnormal occurrence.

9 June 2017, 18 June 2017, 19 June 2017, 29 June 2017 _ Schedule 5 Notification was submitted due to elevated CO readings.

4 July 2017, 21 July 2017, 24 July 2017, 28 July 2017, 31 July 2017 _ Schedule 5 Notification was submitted due to elevated CO readings.

19 December 2017 _ Schedule 5 Notification was submitted due to elevated HCl reading.

##### Table 1: Emissions to Air from A1 and A2 (CEMS)

|  | Releases to Air from Incinerators – Continuous Monitoring – Air 2 |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Parameter |  | Limit | Reference Period | A1 |  | A2 |  |  | Test Method | Uncertainty |
|  |  |  |  | 2017 Max | 2017 Avg | 2017 Max | 2017 Avg |  |  |  |
| Oxides of nitrogen |  | 200 mg/m3 | Daily mean | 199.4 | 174.6 | 268.8 | 182 |  | BS EN 15267-3 |  |
|  |  | 400 mg/m3 | ½ hourly mean | 299.1 |  | 332.0 |  |  |  |  |
| Particulate Matter |  | 10 mg/m3 | Daily mean | 0.8 | 0.6 | 0.5 | 0.4 |  |  |  |
|  |  | 30 mg/m3 | ½ hourly mean | 1.2 |  | 1 |  |  |  |  |
| Total Organic Carbon (TOC) |  | 10 mg/m3 | Daily mean | 1.2 | 0.4 | 1.1 | 0.3 |  |  |  |
|  |  | 20 mg/m3 | ½ hourly mean | 14.7 |  | 19.9 |  |  |  |  |
| Hydrogen chloride |  | 10 mg/m3 | Daily mean | 10.0 | 8.0 | 10.9 | 8.3 |  |  |  |
|  |  | 60 mg/m3 | ½ hourly mean | 34.4 |  | 76.7 |  |  |  |  |
| Sulphur dioxide |  | 50 mg/m3 | Daily mean | 36.3 | 12.1 | 24.1 | 6.3 |  |  |  |
|  |  | 200 mg/m3 | ½ hourly mean | 102.9 |  | 93.0 |  |  |  |  |
| Carbon monoxide |  | 50 mg/m3 | Daily mean | 356.3 | 11.6 | 220.6 | 11.1 |  |  |  |
|  |  | 100 mg/m3 | ½ hourly mean* | See | note | below | --- |  |  |  |
| Ammonia |  | No limit set | Daily mean | 0 | 0 | 6.0 | 1.3 |  |  |  |

##### *Note. ½ hourly monitoring for CO is no longer required in the latest version of the permit. Permit now states “95%ile 10 minute average in any 24 hour period”.

##### *Note: CEMS data figures are adjusted for the method uncertainty

##### Table 2: Emissions to Air from A1 and A2 Periodic

| Substance / Parameter | # Emission Limit Value | A1 | A2 |
| --- | --- | --- | --- |
| ### Nitrous oxide | None set mg/m3 | 7.50 | 10.05 |
| ### Hydrogen fluoride | 2 mg/m3 | 0.03 | 0.03 |
| ### Cd and Th and their compounds | 0.05 mg/m3 | 0.0019 | 0.0014 |
| Hg and its compounds | 0.05 mg/m3 | 0.0038 | 0.0037 |
| Sb, As, Pb, Cr, Co, Cu, Mn, Ni, V and their compounds | 0.5 mg/m3 | 0.034 | 0.015 |
| ### Dioxins & Furans (I-TEQ) | 0.1 ng/m3 | 0.030 | 0.009 |
| PCBs (WHO-TEQ Humans / Mammals) | None set ng/m3 | 0.00254 | 0.00075 |
| PCBs (WHO-TEQ Fish) | None set ng/m3 | 0.00012 | 0.00004 |
| PCBs (WHO-TEQ Birds) | None set ng/m3 | 0.00448 | 0.00210 |
| Dioxins & Furans (WHO-TEQ Humans / Mammals) | None set ng/m3 | 0.0282 | 0.0086 |
| Dioxins & Furans (WHO-TEQ Fish) | None set ng/m3 | 0.0310 | 0.0091 |
| Dioxins & Furans (WHO-TEQ Birds) | None set ng/m3 | 0.0501 | 0.0139 |
| Anthanthrene | None set µg/m3 | <0.012 | <0.011 |
| Benzo(a)anthracene | None set µg/m3 | <0.012 | <0.011 |
| Benzo(a)pyrene | None set µg/m3 | 0.0175 | <0.011 |
| Benzo(b)fluoranthene | None set µg/m3 | <0.012 | <0.011 |
| Benzo(b)naptho(2,1-d) thiophene | None set µg/m3 | <0.012 | <0.011 |
| Benzo(c)phenanthrene | None set µg/m3 | <0.012 | <0.011 |
| Benzo(ghi)perylene | None set µg/m3 | <0.012 | <0.011 |
| Benzo(k)fluoranthene | None set µg/m3 | <0.012 | <0.011 |
| Cholanthrene | None set µg/m3 | <0.012 | <0.011 |
| Chrysene | None set µg/m3 | <0.012 | <0.011 |
| Cyclopenta(cd)pyrene | None set µg/m3 | <0.012 | <0.011 |
| Dibenzo(ai)pyrene | None set µg/m3 | <0.012 | <0.011 |
| Dibenzo(ah)anthracene | None set µg/m3 | <0.012 | <0.011 |
| Fluoranthene | None set µg/m3 | 0.100 | 0.605 |
| Indeno(123-cd) pyrene | None set µg/m3 | <0.015 | <0.011 |
| Naphthalene | None set µg/m3 | 1.100 | 0.655 |
| ##### Note [1]: Where LOD was observed on all sampling events; the max LOD result was used for the average |  |  |  |

# 3.	Point Source Emissions to Water

## 3.1.	Introduction

Permit Condition 3.5.1(a) and Table S3.2 requires Viridor to ensure sample point W1 is free of oil, grease and visible solids

## 3.2	Commentary on Data

Routine sampling was undertaken at W1 during 2017.

## 3.3	Schedule Notices Issued

No Permit limit exceedances were recorded during the review period for emissions to water.

# 4.	Residue Quality Monitoring Requirements

## 4.1.	Introduction

Permit Condition 3.5.1(c) and Table S3.5 require Viridor to undertake residue quality monitoring at minimum monthly intervals for both bottom ash and air pollution control residues.

## 4.2	Commentary on Data

Incinerator Bottom Ash

Figures shown are an average of the analysis undertaken during 2017 which have followed the criteria laid out in the ESA protocol (i.e. 24 samples per year).

Air Pollution Control Residues

Figures shown in Table 3 are an average of the analysis undertaken during 2017.

##### Table 3: Residue Quality

| ### Residue quality |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ### Parameter | ### Limit | ### Normal Operation |  |  |  |  |  | ### Before use of a new disposal or recycling route |  |  |  |
|  |  | ### Bottom ash |  |  | ### APC Residues |  |  | ### Bottom ash ### (Soluble fractions) |  | ### APC Residues ### (Soluble fractions) |  |
|  |  | ### Composite |  |  | ### Line 1 | ### Line 2 |  | ### Line 1 | ### Line 2 | ### Line 1 | ### Line 2 |
| ### Total Organic Carbon | ### 3% | ### 1.5 |  |  |  |  |  |  |  |  |  |
| Antimony (mg/kg) | ### --- | 146.9 |  |  | 953.5 | 1,095.8 |  |  |  |  |  |
| Cadmium (mg/kg) | ### --- | 15.3 |  |  | 270.3 | 273.3 |  |  |  |  |  |
| Thallium (mg/kg) | ### --- | 0.11 |  |  | 1.08 | 1.05 |  |  |  |  |  |
| Mercury (mg/kg) | ### --- | <0.5 |  |  | 7.26 | 6.52 |  |  |  |  |  |
| Lead (mg/kg) | ### --- | 601.3 |  |  | 2136.3 | 2161.3 |  |  |  |  |  |
| Chromium (mg/kg) | ### --- | 145.9 |  |  | 60.5 | 50.0 |  |  |  |  |  |
| Copper (mg/kg) | ### --- | 1800 |  |  | 602.8 | 598.8 |  |  |  |  |  |
| Manganese (mg/kg) | ### --- | 958.5 |  |  | 392.8 | 411.5 |  |  |  |  |  |
| Nickel (mg/kg) | ### --- | 78.6 |  |  | 19.4 | 15.1 |  |  |  |  |  |
| Arsenic (mg/kg) | ### --- | 14.8 |  |  | 71.5 | 77.3 |  |  |  |  |  |
| Cobalt (mg/kg) | ### --- | 31.8 |  |  | 6.5 | 5.4 |  |  |  |  |  |
| Vanadium (mg/kg) | ### --- | 39.2 |  |  | 12.1 | 10.7 |  |  |  |  |  |
| Zinc (mg/kg) | ### --- | 2800.2 |  |  | 13180 | 13297.5 |  |  |  |  |  |
| ### Dioxins/Furans ITEQ (ng/kg) | ### --- | ### 13.7 |  |  | ### 611.0 | ### 1125.7 |  |  |  |  |  |
| ### PCB (WHO-TEQ) Humans (ng/kg) | ### --- | ### 1.22 |  |  | ### 38.6 | ### 32.46 |  |  |  |  |  |
| ### Total soluble fraction (%) | ### --- |  |  |  |  |  |  |  |  |  |  |
| ### Metals only soluble fraction (%) | ### --- |  |  |  |  |  |  |  |  |  |  |

# 5.	Performance Parameters

5.1 Introduction

Condition 4.2.2 (b), (c), Table S4.2 and S4.3 of the Permit set out the reporting criteria for performance parameters.

5.2 Commentary on Data

The recorded performance data is set out in Tables 4; 5; 6 and 7.

Table 4: Energy 1

| Parameter | Total (MWh) | Specific usage (MW / tonne incinerated) |
| --- | --- | --- |
| Electricity generated | 258,111 | 0.71 |
| Electricity exported to the National Grid | 231,062 | 0.64 |
| Energy exported as heat (if any) | 0 | 0 |
| Energy usage | 27,049 | 0.07 |

Using waste incinerated = 363,155 tonnes.

Table 5: Performance 1

| Parameter | Units |  |
| --- | --- | --- |
| Total municipal (domestic household) waste received on site | Tonnes | 280,842 |
| Total commercial and industrial waste received on site | Tonnes | 83,262 |
| Municipal waste incinerated | Tonnes | 280,216 |
| Commercial and industrial waste incinerated | Tonnes | 82,938 |
| Total waste incinerated | Tonnes | 363,155 |
| Unsuitable waste sent off-site for treatment | Tonnes | 4 |
| Rejected material sent for off-site disposal | Tonnes | 3 |
| Gas oil consumption | Tonnes | 387.1 |
| Dry Urea Reagent usage | kg/tonne waste incinerated | 1.26 |
| Hydrated Calcium Hydroxide Reagent usage | kg/tonne waste incinerated | 14.83 |
| Activated carbon used | kg/tonne waste incinerated | 0.26 |

Table 6: Water Usage 1

| Parameter | Units |  |
| --- | --- | --- |
| Mains water usage | m3 | 20,142 |
| Mains water usage | Litres/tonne waste incinerated | 55.5 |

Table 7: Residues

| Parameter | Units |  |
| --- | --- | --- |
| Total Air Pollution Control residues disposed of | kg/tonne waste incinerated | 25.09 |
| Total bottom ash generated | kg/tonne waste incinerated | 208.92 |
| Total bottom ash recycled | kg/tonne waste incinerated | 208.92 |
| Total bottom ash disposed of | kg/tonne waste incinerated | 0 |