The Environmental Permitting (England and Wales) Regulations 2010

Permit: EPR/LP3030XA Cardiff Energy Recovery Facility

Annual Performance Report 2019

Prepared by: Viridor Waste Management, Trident Park ERF, Glass Avenue, Cardiff. CF24 5EN

Version: 2.0 Issue Date: 30/03/2020

Quality Assurance

This report has been prepared with all reasonable skill, care and diligence. Information reported herein is based on the interpretation of data collected and has been accepted in good faith as being accurate and valid.

|  | Report Details |  |  |
| --- | --- | --- | --- |
|  | Report Title: | Cardiff Energy Recovery Facility - Annual Performance Report 2019 |  |
|  | Report Date: | 30/03/2020 |  |
|  | Version: | 2 |  |
|  | Report Generated By |  |  |
|  | Name: | Pip Crabbe |  |
|  | Position: | EHS Assistant |  |
|  | Report Approved By |  |  |
|  | Name: | Gwyn Jones |  |
|  | Position: | EHS Manager |  |

## 1. 	Introduction

Cardiff Energy Recovery Facility is located immediately north of Cardiff Docks. The facility will process approximately 22.96 tonnes of residual municipal and C&I waste per line, per hour and has the capability of exporting approximately 30MW of electrical power.

In accordance with the requirements of Condition 4.2.2, Schedule 4 and Table S4.1 of Permit EPR/LP3030XA issued by Natural Resources Wales to Viridor Waste Management Limited (Viridor) on 4th November 2010, Viridor is required to produce an annual performance report which is to be submitted to Natural Resources Wales by the 30th April as agreed in writing with Natural Resources Wales of each year.

Viridor took over the operation of the Plant on 31st January 2015; therefore the 2019 Report is the fifth document.

This report summarises the environmental and performance data collected at the site 1st January 2019 – 31st December 2019 and fulfils the reporting requirement of Chapter IV, Article 55 (2) of the Industrial Emissions Directive.

The report will cover the following areas of environmental monitoring:

Section 2 – Point Source Emissions to Air

Section 3 – Point Source Emissions to Water

Section 4 – Residue Quality Monitoring Requirements

Section 5 – Performance Parameters

# 2.	Point Source Emissions to Air

## 2.1.	Introduction

Permit Condition 3.5.1(a) and Tables S3.1 and S3.1(a) require Viridor to undertake performance monitoring of the point source emissions to air arising at sample points A1 and A2.

A summary of the point source emissions to air monitoring data at sample point A1 and A2 for the period is included as Table 1.

## 2.2	Commentary on Data

The recorded concentrations remained compliant with the limits set out in Permit Tables S3.1 and S3.1 (a) during the review period with the exception of those listed in 2.3.

Line 1 was in operation for 88.9% of the year and Line 2 for 87.9%.

Note 1: Detail of periodic sampling timings, uncertainty and method used have previously been supplied to Natural Resources Wales within the 2019 quarterly reports.

Note 2: Results recorded by both, periodic and continuous monitoring have broadly been within the range expected for the energy recovery operation, with exception to the exceedances included in 2.3 below.

## 2.3	Schedule Notices Issued

Q1

Part A notification reported on	10 January 2019

Date of event 				09 January 2019

Parameter 				CO (daily mean) reading on Line 2.

Part A notification submitted on	15 February 2019

Date of event				13 February 2019

Event					Elevated HCl (1/2 hour mean) reading on Line 1.

Part C Notification reported on	8 March 2019 (after discussions with NRW)

Date of event				5 March 2019

Details	Abnormal operation on Line 2.  At 20:30H on Tuesday 5 March 2019, there was a failure of communication between the Distributed Control System (DCS) and the Continuous Emissions Monitoring System (CEMS).

Q2

Part A notification reported on	30 April 2019

Date of event 				Started 28 April 2019 at 18:09H

Details 				Elevated CO (95%’ile 10 minute average over

ANY 24 hour period) on Line 2.  8 exceedances occurred when allowed 7.2 exceedances.

Part C notification submitted on	7 May 2019

Date of event				4 May 2019

Event					Abnormal operation – lime dosing tripped for 38

Minutes

Part A notification reported on	15 May 2019

Date of event 				13 May 2019

Details 				Line 1 CO daily average

Line 1 VOC ½ hourly average

Part A Notification reported on	16 May 2019

Date of event				Started on 25 April 2019 at 22:00H

Event					Elevated CO (95%’ile 10 minute average over

ANY 24 hour period) on Line 2.  10 exceedances occurred when allowed 7.2 exceedances.

Q3

Part A Notification reported on 	22 July 2019

Date of Event 				Started 21 July 2019 at 16:40H

Details 				Elevated CO (95%’ile 10 minute average over

ANY 24 hour period) on Line 2.  8 exceedances occurred when allowed 7.2 exceedances.

Part A reported on 			19 August 2019

Date of Event 				19 August 2019 between 08:30H and 08:59H.

Details 	S02 exceedance via Stream 1 Exceeding the permissible ELV 1/2hourly average.

Q4

Part C notification reported on	04 November 2019

Date of event 				Started 4 November 2019 at 02:30H

Details 				Abatement plant failed – Urea dosing

½ hour exceedance from 02:30H to 02:59H

Recorded 402.1mg/m3 when ELV = 400mg/m3

##### Table 1: Emissions to Air from A1 and A2 (CEMS)

|  | Releases to Air from Incinerators – Continuous Monitoring – Air 2 |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Parameter |  | Limit | Reference Period | A1 |  | A2 |  |  | Test Method | Uncertainty |
|  |  |  |  | Max | Avg | Max | Avg |  |  |  |
| Oxides of nitrogen |  | 200 mg/m3 | Daily mean | 207.15 | 182.2 | 203.775 | 180.55 |  | BS EN 15267-3 |  |
|  |  | 400 mg/m3 | ½ hourly mean | 349.825 |  | 255.65 |  |  |  |  |
| Particulate Matter |  | 10 mg/m3 | Daily mean | 0.625 | 0.525 | 0.45 | 0.375 |  |  |  |
|  |  | 30 mg/m3 | ½ hourly mean | 1.525 |  | 0.65 |  |  |  |  |
| Total Organic Carbon (TOC) |  | 10 mg/m3 | Daily mean | 0.625 | 0.2 | 0.925 | 0.133 |  |  |  |
|  |  | 20 mg/m3 | ½ hourly mean | 13 |  | 9.225 |  |  |  |  |
| Hydrogen chloride |  | 10 mg/m3 | Daily mean | 10.625 | 8.5 | 10.225 | 8.375 |  |  |  |
|  |  | 60 mg/m3 | ½ hourly mean | 44.6 |  | 48.2 |  |  |  |  |
| Sulphur dioxide |  | 50 mg/m3 | Daily mean | 42.025 | 23.525 | 23.5 | 11.55 |  |  |  |
|  |  | 200 mg/m3 | ½ hourly mean | 144.1 |  | 78.65 |  |  |  |  |
| Carbon monoxide |  | 50 mg/m3 | Daily mean | 33.475 | 8.175 | 51.3 | 8.375 |  |  |  |
|  |  | 100 mg/m3 | ½ hourly mean* |  |  |  |  |  |  |  |
| Ammonia |  | No limit set | Daily mean | 2.1 | 2.1 | 5.2 | 2.125 |  |  |  |

##### *Note. ½ hourly monitoring for CO is no longer required in the latest version of the permit

##### *Note: CEMS data figures are adjusted for the method uncertainty

##### Table 2: Emissions to Air from A1 and A2 Periodic (H1 and H2 combined average)

| Substance / Parameter | # Emission Limit Value | A1 | A2 |
| --- | --- | --- | --- |
| ### Nitrous oxide | None set mg/m3 | 7.97 | 8.85 |
| ### Hydrogen fluoride | 2 mg/m3 | 0.03 | 0.04 |
| ### Cd and Th and their compounds | 0.05 mg/m3 | 0.0008 | 0.0005 |
| Hg and its compounds | 0.05 mg/m3 | 0.0023 | 0.00155 |
| Sb, As, Pb, Cr, Co, Cu, Mn, Ni, V and their compounds | 0.5 mg/m3 | 0.04925 | 0.0272 |
| ### Dioxins & Furans (I-TEQ) | 0.1 ng/m3 | 0.024 | 0.01402 |
| PCBs (WHO-TEQ Humans / Mammals) | None set ng/m3 | 0.0011225 | 0.000875 |
| PCBs (WHO-TEQ Fish) | None set ng/m3 | 0.000087 | 0.000065 |
| PCBs (WHO-TEQ Birds) | None set ng/m3 | 0.0036285 | 0.00257 |
| Dioxins & Furans (WHO-TEQ Humans / Mammals) | None set ng/m3 | 0.02515 | 0.061 |
| Dioxins & Furans (WHO-TEQ Fish) | None set ng/m3 | 0.0268 | 0.01615 |
| Dioxins & Furans (WHO-TEQ Birds) | None set ng/m3 | 0.0339 | 0.019075 |
| Anthanthrene | None set µg/m3 | <0.00625 | <0.00685 |
| Benzo(a)anthracene | None set µg/m3 | <0.00625 | <0.00685 |
| Benzo(a)pyrene | None set µg/m3 | <0.00625 | <0.00685 |
| Benzo(b)fluoranthene | None set µg/m3 | <0.00625 | <0.00685 |
| Benzo(b)naptho(2,1-d) thiophene | None set µg/m3 | <0.0135 | <0.0074 |
| Benzo(c)phenanthrene | None set µg/m3 | <0.0135 | <0.0074 |
| Benzo(ghi)perylene | None set µg/m3 | <0.00625 | <0.00685 |
| Benzo(k)fluoranthene | None set µg/m3 | <0.00625 | <0.0074 |
| Cholanthrene | None set µg/m3 | <0.0135 | <0.0074 |
| Chrysene | None set µg/m3 | <0.00625 | <0.01015 |
| Cyclopenta(cd)pyrene | None set µg/m3 | <0.00675 | <0.0074 |
| Dibenzo(ai)pyrene | None set µg/m3 | <0.00725 | <0.12285 |
| Dibenzo(ah)anthracene | None set µg/m3 | <0.00625 | <0.0167 |
| Fluoranthene | None set µg/m3 | 0.003 | 0.015 |
| Indeno(123-cd) pyrene | None set µg/m3 | <0.00625 | <0.0167 |
| Naphthalene | None set µg/m3 | 0.32 | 0.405 |
| ##### Note [1]: Where LOD was observed on all sampling events; the max LOD result was used for the average |  |  |  |

# 3.	Point Source Emissions to Water

3.1.	Introduction

Permit Condition 3.5.1(a) and Table S3.2 requires Viridor to ensure sample point W1 is free of oil, grease and visible solids.

3.2	Commentary on Data

During the year 2020 monitoring point W1 has remained free of oil and grease.

3.3	Schedule Notices Issued

No Permit limit exceedances were recorded during the review period for emissions to water.

# 4.	Residue Quality Monitoring Requirements

## 4.1.	Introduction

Permit Condition 3.5.1(c) and Table S3.5 require Viridor to undertake residue quality monitoring at minimum monthly intervals for both bottom ash and air pollution control residues.

## 4.2	Commentary on Data

Incinerator Bottom Ash

Figures shown are an average of the analysis undertaken during 2019 which have followed the criteria laid out in the ESA protocol.

Air Pollution Control Residues

Figures shown in Table 3 are an average of the analysis undertaken during 2019.

##### Table 3: Residue Quality

| ### Residue quality |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ### Parameter | ### Limit | ### Normal Operation |  |  |  |  |  | ### Before use of a new disposal or recycling route |  |  |  |
|  |  | ### Bottom ash |  |  | ### APC Residues |  |  | ### Bottom ash ### (Soluble fractions) |  | ### APC Residues ### (Soluble fractions) |  |
|  |  | ### Composite |  |  | ### Line 1 | ### Line 2 |  | ### Line 1 | ### Line 2 | ### Line 1 | ### Line 2 |
| ### Total Organic Carbon | ### 3% | ### 1.15 |  |  |  |  |  |  |  |  |  |
| Antimony (mg/kg) | ### --- | 279.5 |  |  | 981 | 847.5 |  |  |  |  |  |
| Cadmium (mg/kg) | ### --- | 29.15 |  |  | 275.5 | 274.75 |  |  |  |  |  |
| Thallium (mg/kg) | ### --- | <0.1 |  |  | 0.925 | 0.8 |  |  |  |  |  |
| Mercury (mg/kg) | ### --- | <0.5 |  |  | 7.1675 | 8.3425 |  |  |  |  |  |
| Lead (mg/kg) | ### --- | 666.275 |  |  | 1616 | 4411.25 |  |  |  |  |  |
| Chromium (mg/kg) | ### --- | 132.75 |  |  | 43.675 | 37.35 |  |  |  |  |  |
| Copper (mg/kg) | ### --- | 1717.4 |  |  | 607.25 | 538.25 |  |  |  |  |  |
| Manganese (mg/kg) | ### --- | 1170 |  |  | 384.75 | 363.25 |  |  |  |  |  |
| Nickel (mg/kg) | ### --- | 68.65 |  |  | 14.525 | 13.775 |  |  |  |  |  |
| Arsenic (mg/kg) | ### --- | 25.95 |  |  | 61.075 | 59.825 |  |  |  |  |  |
| Cobalt (mg/kg) | ### --- | 31.55 |  |  | 4.675 | 3.9 |  |  |  |  |  |
| Vanadium (mg/kg) | ### --- | 38.775 |  |  | 17.8 | 17.2 |  |  |  |  |  |
| Zinc (mg/kg) | ### --- | 3605.35 |  |  | 15262.5 | 12965 |  |  |  |  |  |
| ### Dioxins (top) /Furans (bottom) ITEQ (ng/kg) | ### --- | ### 5.061 ### 6.059 |  |  | ### 165.394 ### 232.085 | ### 162.981 ### 213.061 |  |  |  |  |  |
| ### PCB (WHO-TEQ) Humans (ng/kg) | ### --- | ### 2.032 |  |  | ### 6.924 | ### 8.981 |  |  |  |  |  |
| ### Total soluble fraction (%) | ### --- |  |  |  |  |  |  |  |  |  |  |
| ### Metals only soluble fraction (%) | ### --- |  |  |  |  |  |  |  |  |  |  |

Please note.  The units used for Dioxin Furan and PCBs are in ng/m3 whilst the units for other determinants (except TOC) are in mg/m3.

# 5.	Performance Parameters

5.1 Introduction

Condition 4.2.2 (b), (c), Table S4.2 and S4.3 of the Permit set out the reporting criteria for performance parameters.

5.2 Commentary on Data

The recorded performance data is set out in Tables 4; 5; 6 and 7.

Table 4: Energy 1

| Parameter | Total (MWh) | Specific usage (MW / tonne incinerated) |
| --- | --- | --- |
| Electricity generated | 257,132 | 0.70 |
| Electricity exported to the National Grid | 230,251 | 0.62 |
| Energy exported as heat (if any) | 0 | 0 |
| Energy usage (909MWh brought onto site from National Grid + 26,881MWh parasitic off take) | 27,790 | 0.07 |

Table 5: Performance 1

| Parameter | Units |  |
| --- | --- | --- |
| Total municipal (domestic household) waste received on site | Tonnes | 272,459 |
| Total commercial and industrial waste received on site | Tonnes | 97,287 |
| Municipal waste incinerated | Tonnes | 266,854 |
| Commercial and industrial waste incinerated | Tonnes | 98,788 |
| Total waste incinerated | Tonnes | 365,643 |
| Unsuitable waste sent off-site for treatment | Tonnes | 0 |
| Rejected material sent for off-site disposal | Tonnes | 27.14 |
| Gas oil consumption 373,329 litres (conv factor litres to kg = 0.91) = (339.7 tonnes) | Tonnes | 339.7 |
| Dry Urea Reagent usage (462 tonnes) | kg/tonne waste incinerated | 1.26 |
| Hydrated Calcium Hydroxide Reagent usage (4791 tonnes) | kg/tonne waste incinerated | 13.1 |
| Activated carbon used (113 tonnes) | kg/tonne waste incinerated | 0.31 |

Table 6: Water Usage 1

| Parameter | Units |  |
| --- | --- | --- |
| Mains water usage | m3 | 61,241 |
| Mains water usage 61,241 x 1000L /365,643 | Litres/tonne waste incinerated | 167.48 |

Table 7: Residues

| Parameter | Units |  |
| --- | --- | --- |
| Total Air Pollution Control residues disposed of (11,940.9T) | kg/tonne waste incinerated | 32.65 |
| Total bottom ash generated (73,561.29T) | kg/tonne waste incinerated | 201.18 |
| Total bottom ash recycled | kg/tonne waste incinerated | 201.18 |
| Total bottom ash disposed of | kg/tonne waste incinerated | 0 |