## Cover Page
Add company logo
Version 24.1a (for incinerators) - 08/11/24
Note that there is another version of this template available for co-incinerators
Add photo
Notes:
This template may require adjustments by individual operators to meet specific reporting requirements as defined in the site Permit(s)
Annual Performance Report 2024
Permit EPR/SP3239FU
Enfinium Ferrybridge 1 Limited
enfinium Ferrybridge 1 Ltd
Year: | 2024
Address: | Kirkhaw Lane, Knottingley, West Yorkshire, WF11 8DX
Tel: | 07385 473628
Email: | lee.leonards@enfinium.co.uk
Prepared by: | Lee Leonards |  | Position: | Environmental Manager
Approved by: | Steve Tosney |  | Position: | Plant Manager
Version: | 1
Issue Date: | 2025-01-30
Print Report
Print as PDF

## Facility Info
Annual Performance Report 2024 | Enfinium Ferrybridge 1 Limited
Plant Description and Design |  | Notes:
Ferrybridge 1 is designed for the disposal of waste with energy recovery in an incineration plant and is permitted under Section 5.1 A(1)(b) the incineration of non-hazardous waste in an incineration plant with a capacity exceeding 3 tonnes per hour. The installation is located on land adjacent to the Ferrybridge Power Station site, close to the A1(M). It lies 1km northwest of the village of Ferrybridge, 2km northwest of Knottingley, 1.9km southeast of Ferry Fryston, and 3km northeast of Pontefract, at grid reference SE 4726 2500. The facility has a throughput limit of 725,000 tonnes per year of waste which can include refuse derived fuel, waste wood and commercial and industrial waste. The facility consists of two combustion lines and generates approximately 80 MWe of electricity, of which approximately 73 MWe is exported. Moving grate technology is used for burning the waste material. The furnace design ensures that a temperature of at least 850 degrees Celsius for a period of at least two seconds is achieved in the combustion chamber. Auxiliary burners firing a low sulphur gas oil are automatically triggered by online process monitoring equipment are used to ensure the temperature does not fall below 850 degrees Celsius. Hot gases from the furnace pass into a boiler. Steam raised in the boiler is passed to a turbine to generate electricity for export to the National Grid. |  | Include summary of plant design, design capacity, no. of combustion lines, electrical and heat capacity and any other general information that describes the facility, its location and purpose
Summary of Operational Processes and Procedures
"Key processes include waste reception, waste storage, water use, drainage, flue gas and air supply systems, boilers, treatment of exhaust gases, treatment and storage of residues and water recycling, stacks, devices and systems for controlling incineration operations, recording and monitoring conditions. The site has an Environmental Management System accredited to ISO 14001. The site has a Health and Safety management system covering all aspects of health and safety which is accredited to ISO 45001. Maintenance across the facilities is broken down in to reactive (breakdown) maintenance, and planned preventive maintenance. Preventive maintenance is conducted via the philosophy of Risk Based Inspections to ensure the safety of personnel and availability of the plant is cost effectively maintained." |  | Include summary of key processes and procedures such as (but not limited to); waste reception, control rooms, grate, bed and boiler, energy & heat generation, cooling systems, residue management, emission controls, health and safety systems, maintenance

## Contents
Annual Performance Report 2024 |  | Enfinium Ferrybridge 1 Limited
Contents |  |  |  | Notes:
Section | Subject |  | Page | Section references and Page nos. to be inserted
| Facility Information |  | 2 | Sections and Subjects may require adjustment by individual operators to meet specific reporting requirements as defined in the sites Permit(s)
| Operational Data |  | 4
| Operational Summary |  | 5
| Performance Form 1 |  | 6
| Energy Form 1 |  | 8
| Permit Compliance |  | 9
| Improvements |  | 11
| Public Liaison |  | 12
| Carbon dioxide and nitrous oxide emissions |  | 13
| Residue Quality |  | 14
| Emissions to Water |  | 15
| Emissions to Air (periodically monitored) |  | 16
| Emissions to Air (continuously monitored) |  | 18
| Hydrogen Chloride emissions |  | 19
| Sulphur Dioxide emissions |  | 20
| Oxides of Nitrogen emissions |  | 21
| Total Organic Carbon emissions |  | 22
| Particulate Matter emissions |  | 23
| Carbon Monoxide emissions |  | 24
| Ammonia emissions |  | 25
Version Control
Section | Information |  | Date
Distribution
Copy | Name, Role |  | No.
This report is required under the Industrial Emissions Directive’s Article 55(2) requirements on reporting and public information on waste incineration plants and co-incineration plants, which require the operator to produce an annual report on the functioning and monitoring of the plant and make it available to the public.

## Operational Data
Annual Performance Report 2024 |  |  |  | Enfinium Ferrybridge 1 Limited
Operational Data
Plant Size | 725000 |  | tonnes pa | 80 | MWth | 73 | MWe |  | Notes:
No. of combustion lines | 2 |  | No. of Turbines: |  | 1 |  |  |  | * - RDF to include SRF
** - Combusted tonnage = tonnes delivered in period + (tonnes in bunker at start of period – tonnes in bunker at end of period), or equivalent calculation depending on plant type
Waste types received | Unit | Q1 | Q2 | Q3 | Q4 | Year Total | %
Household / Local Authority | tonnes | 7668.5 | 14211 | 14683.08 | 14636.42 | 51199 | 7.837%
Commercial & Industrial | [5 empty] | 0 | - |  | *** - CHP plants only
Hazardous | [5 empty] | 0 | - |  | **** Availability Definition: 'the availability of a line is to be calculated by the number of hours the line reported Continuously Monitored emission levels to the Regulator through the calendar year divided by the total number of hours in that year. The overall plant availability is calculated as the Mean of all lines in the plant. For clarity this includes periods of abnormal operation.' Rationale: The primary function of an Energy from Waste facility is the disposal of waste. It follows therefore that the availability of a plant is determined by the period of time a facility spends undertaking this activity.
Clinical | [5 empty] | 0 | -
Waste wood (biomass) | [5 empty] | 0 | -
Refuse Derived Fuel * - H'hold/LA |  | 163750.24 | 122011.98 | 156974.24 | 159343.8 | 602080.26 | 92.16%
Refuse Derived Fuel * - C&I | [5 empty] | 0 | -
Other [Please specify] | [5 empty] | 0 | -
Other [Please specify] | [5 empty] | 0 | -
Other [Please specify] | [5 empty] | 0 | -
Total waste received |  | 171418.74 | 136222.98 | 171657.32 | 173980.22 | 653279.26
Rejected Waste | [5 empty] | 0 | -
Unprocessed waste transferred out |  | 19.98 | 23.96 | 29 | 9.5 | 82.44 | 0.01262%
Total waste combusted ** |  | 169754.72 | 138529.94 | 165878.52 | 177177.53 | 651340.71
Password for protected cells A password has been set to prevent accidental editing of cells with formulae. If you still need to make an edit for some reason then the password = 1234
Energy Usage / Export | Unit | Q1 | Q2 | Q3 | Q4 | Year Total | KWh/te
Power Generated | MWh | 166893.87 | 134042.49 | 169533.32 | 175824.9 | 646294.58 | 992.2527
Power Exported |  | 152368 | 122900 | 153241 | 159176 | 587685 | 902.2697
Power Used on site |  | 14525.87 | 11142.49 | 16292.32 | 16648.9 | 58609.58 | 89.983
Power Imported |  | 125.34 | 482.9 | 34.9 | 31.85 | 674.99 | 1.0363
Parasitic Load | % | 8.772% | 8.642% | 9.629% | 9.485% | 9.163%
Thermal Energy Produced *** | MWh |  |  |  |  | 0 | -
Thermal Energy Exported *** | [5 empty] | 0 | -
R1 value (if applicable) | R1 |  |  |  |  | 0.848
Waste Disposal & Recovery | Unit | Q1 | Q2 | Q3 | Q4 | Year Total | % inputs
APC Residues - produced | tonnes | 6123.95 | 5039.38 | 6417.24 | 5843.54 | 23424.11 | 3.596%
Waste oil |  | 1.69 | 0.89 |  | 1.38 | 3.96 | 0.000608%
Oil contaminated solid waste |  |  | 4.4 |  | 7.82 | 12.22 | 0.001876%
APCr filter bags |  |  | 25.34 |  |  | 25.34 | 0.00389%
Fluorescent tubes |  |  |  |  | 1 | 1 | 0.0001535%
Lab chemicals |  |  |  |  | 0.665 | 0.665 | 0.0001021%
IBA - produced |  | 31940.46 | 25834.83 | 32735.22 | 31213.6 | 121724.11 | 18.69%
Metals recycling |  | 1174.92 | 1061.08 | 1114.08 | 1021.12 | 4371.2 | 0.6711%
Dry Mixed Recyclables |  | 0.84 | 5.08 | 1 | 1.68 | 8.6 | 0.00132%
General Waste |  | 4.72 | 15.66 | 8.02 | 0.3 | 28.7 | 0.004406%
Wood |  | 5.26 | 4.54 | 4.58 | 1.5 | 15.88 | 0.002438%
Rubble |  | 30.24 | 30.36 | 14.42 | 8.02 | 83.04 | 0.01275%
Aqueous Waste |  | 654.28 | 87.51 |  | 143.46 | 885.25 | 0.1359%
Sewage |  | 5.5 | 173.34 | 13.86 | 66.58 | 259.28 | 0.03981%
Electrical Components |  |  |  | 2.14 | 1.5 | 3.64 | 0.0005588%
Other |  | 0 | 0 | 0 | 0 | 0 | -
Raw Material Usage | Unit | Q1 | Q2 | Q3 | Q4 | Year Total | kg or Ltr /te
Mains Water | ltrs | 21027000 | 24866000 | 22202000 | 24275000 | 92370000 | 141.8152
Other Water | ltrs | 16033560 | 11263830 | 15410000 | 16535000 | 59242390 | 90.9545
Ammonia | kgs | 24404.24 | 4957.49 | 691.25 | 5049.86 | 35102.84 | 0.053893
Urea | kgs | 0 |  |  |  | 0 | -
Activated Carbon | kgs | 40057 | 33999 | 49976 | 46984 | 171016 | 0.26256
Lime / hydrated lime | kgs | 2591610 | 2364630 | 2895700 | 2497763.89 | 10349703.89 | 15.8898
Fuel oil | ltrs | 239143.12 | 303948.06 | 282421.22 | 197850.65 | 1023363.05 | 1.5712
Gas | cuf |  |  |  |  | 0
Other | [5 empty] | 0
Summary | Line/Unit | Q1 | Q2 | Q3 | Q4 | Year Total |  | Hrs in year
Availability of waste combustion by line, hrs **** | 1 | 2080 | 1617 | 2065 | 2099 | 7861 | 89.74% | 8760
| 2 | 1999.8 | 1750.9 | 2089.5 | 2139.2 | 7979.4 | 91.09%
Overall Availability, mean avg. of all lines, hrs |  | 2039.9 | 1683.95 | 2077.25 | 2119.1 | 2039.9 | 23.29%
Hours of turbine operations, hrs | 1 | 2139.8 | 1851 | 2200.6 | 2208 | 8399.4 | 95.88%
Hours of heat / steam export | [5 empty] | 0 | n/a
Net Calorific Value of waste | MJ/kg | 10.73 | 9.99 | 11.7 | 11
Abnormal Events | qty. | 9 |  |  |  | 9 | yes
Abnormal operation | hours | 21.5 |  |  |  | 21.5 | 0.2454%
Permit Breaches | qty. | 0 |  |  |  | 0 | no

## Operational Summary
Annual Performance Report 2024 |  |  |  | Enfinium Ferrybridge 1 Limited
Summary of Plant Operations and Maintenance during the reporting year | [7 empty] | Notes:
Overall, plant operations have been good with very little downtime and issues. Some shutdowns were initiated in order to repair some of the plant equipment, largely the boiler tubes. There have been no issues with emissions limits for the year. Online boiler cleans are carried out roughly every 2 months. A longer than usual outage was planned in March/April 2024 whereby several maintenance projects were undertaken as summarised below: Grate Inspections and Repairs. Removed and replaced 1st/2nd pass dividing wall panels 1st and 2nd Pass Inconel Inspections on Repairs. Replaced filter bags in 11off chambers on Line 2 and 5off chambers on line 1. Full Ash and Residue Systems inspections. Replaced all 4off Ash Extractor Chutes Replaced Line 1 and 2 Feed Hopper Chutes for an upgraded design Completed Statutory PSSR inspections. Full Site Instrumentation calibrations. All site VFD’s Inspected and repairs or replaced where required. Stack and Ducting Inspections and Repairs. | [7 empty] | Include summary of key operational and/or maintenance activity undertaken in the year, such as any major component upgrades and/or replacements
Summary of Residue Handling for the reporting year
"Incinerator Bottom Ash (IBA) from Ferrybridge 1 is stored in the Ash Bunker and then outloaded by the ash crane grab to receiving dumper trucks. The IBA is collected and taken to the Blue Phoenix Ferrybridge site, which is adjacent to the north of the Ferrybridge 2 site. Movement of the IBA is carried out by dumper truck via a predominantly internal road network to the Blue Phoenix site where it is processed into Incinerator Bottom Ash Aggregate (IBAA). APCr is collected in silos and then discharged to receiving tanker for off-site disposal. The APCr is transported to Castle Environmental Ltd and occasionally to OCO Technology. Castle Environmental receives APCr at two sites located in Ilkeston (Derbyshire) and Stoke on Trent, whereas OCO Technology has one site located in Leeds. Castle Environmental currently recycles approximately 70% of the APCr whereas OCO Technology recycles 100%." | [7 empty] | Include in here a summary of residue handling regimes and destinations
2024 | Plant shut-downs
Date | Reason for shut-down | [6 empty] | Provide a very brief reason for plant shut-down e.g. "Shut-down prior to major outage"; "Emergency shut-down due to boiler tube leak" There is no need to include periods of hot-standby here (e.g. to clear feed chute hopper blockages). For clinical waste incinerators which require regular shut-downs for boiler cleaning, there is no need to record these here.
2024-01-16 | Line 2 shutdown to repair a leak to the grate cooling water
2024-03-23 | Line 1 shutdown for boiler tube leak
2024-03-25 | Line 2 was shut-down for its annual major outage
2024-04-03 | Line 1 shutdown for it's annual major outage
2024-04-30 | Line 2 shutdown to repair a boiler tube leak
2024-06-25 | Line 1 shutdown to repair ID fan motor and an ash extracter RAM
2024-08-14 | Line 1 shut down to carry out repairs to refractory tiles, the ID fan motor and the economiser screw
2024-07-10 | Line 2 emergency shut down due to a bag filter failure
2024-09-23 | Line 2 shut down to repair a boiler tube leak
2024-09-27 | Line 1 shut down to repair a boiler tube leak
2024-11-13 | Line 1 shut down to repair a boiler tube leak
2024-12-11 | Line 2 shut down to repair some refactory tiles
2024-12-17 | Line 1 shut down to repair some refactory tiles
2024 | Mercury and dioxins monitoring protocol compliance | [6 empty] | Use this table to record any exceedances of the threshold values under the mercury and dioxins monitoring protocols and the result of the subsequent 2x retests (see protocols). For mercury, the threshold value is 10 µg/m3 (11% oxygen).For dioxins, the threshold value is the permit ELV. Enter N/A in the first date box if there have been no exceedances of the threshold.
Date | Line | Hg or dioxins | Values |  | Measures put in place to prevent recurrence
N/A |  |  | Exceedance
Retest 1
Retest 2
Exceedance
Retest 3
Retest 4
Note that the monitoring protocols require the operator to demonstrate consistent performance below threshold values such that continuous dioxins sampling or mercury monitoring is not required. The threshold value for dioxins is the same as the permit ELV, whereas the threshold for mercury is half of the ELV. Therefore, an exceedance of the threshold value for mercury does not necessarily mean an exceedance of the permit ELV.
Line 1 Duty | Results of annual surveillance tests (ASTs) for continuous emissions monitors | [6 empty] | Use this table to record the results of the annual surveillance tests (ASTs) that are carried out on the continuous emissions monitors (CEMS). Where the CEM passes the AST, enter N/A under all the proceeding cells. Even if a new QAL2 is done as a precautionary measure, an AST must also be completed, and the reasons for any failures investigated. Add additional table(s) if your plant has more than 3 lines.
Date | Monitor | Pass/fail | Root cause of failure |  |  | Date of QAL2 | Date new calibration function entered
01/10/24 | HCl | Pass | N/A |  |  | N/A | N/A
01/10/24 | SO2 | Pass | N/A |  |  | N/A | N/A
01/10/24 | NO | Pass | N/A |  |  | N/A | N/A
01/10/24 | NO2 | Pass | N/A |  |  | N/A | N/A
01/10/24 | TOC | Pass | N/A |  |  | N/A | N/A
01/10/24 | Particulate matter | Pass | N/A |  |  | N/A | N/A
01/10/24 | CO | Pass | N/A |  |  | N/A | N/A
01/10/24 | NH3 | Pass | N/A |  |  | N/A | N/A
01/10/24 | CO2 | Pass | N/A |  |  | N/A | N/A
01/10/24 | N20 | Pass | N/A |  |  | N/A | N/A
01/10/24 | O2 | Pass | N/A |  |  | N/A | N/A
01/10/24 | Moisture | Pass | N/A |  |  | N/A | N/A
01/10/24 | Velocity | Pass | N/A |  |  | N/A | N/A
Line 1 Standby | Results of annual surveillance tests (ASTs) for continuous emissions monitors
Date | Monitor | Pass/fail | Root cause of failure |  |  | Date of QAL2 | Date new calibration function entered
01/10/24 | HCl | Pass | N/A |  |  | N/A | N/A
01/10/24 | SO2 | Fail | Contacted Envea to look into the settings to ensure all correct, checked previous QAL 3 to ensure span and drift were acceptable. Checked for leaks on the system and gas pressures were all ok. |  |  | 2025-01-07 | TBC
01/10/24 | NO | Pass | N/A |  |  | N/A | N/A
01/10/24 | NO2 | Pass | N/A |  |  | N/A | N/A
01/10/24 | TOC | Pass | N/A |  |  | N/A | N/A
01/10/24 | Particulate matter | Pass | N/A |  |  | N/A | N/A
01/10/24 | CO | Pass | N/A |  |  | N/A | N/A
01/10/24 | NH3 | Pass | N/A |  |  | N/A | N/A
01/10/24 | CO2 | Pass | N/A |  |  | N/A | N/A
01/10/24 | N20 | Pass | N/A |  |  | N/A | N/A
01/10/24 | O2 | Pass | N/A |  |  | N/A | N/A
01/10/24 | Moisture | Pass | N/A |  |  | N/A | N/A
01/10/24 | Velocity | Pass | N/A |  |  | N/A | N/A
Line 2 Duty | Results of annual surveillance tests (ASTs) for continuous emissions monitors
Date | Monitor | Pass/fail | Root cause of failure |  |  | Date of QAL2 | Date new calibration function entered
01/10/24 | HCl | Pass | N/A |  |  | N/A | N/A
01/10/24 | SO2 | Fail | Contacted Envea to look into the settings to ensure all correct, checked previous QAL 3 to ensure span and drift were acceptable. Checked for leaks on the system and gas pressures were all ok. |  |  | 2025-01-07 | TBC
01/10/24 | NO | Pass | N/A |  |  | N/A | N/A
01/10/24 | NO2 | Pass | N/A |  |  | N/A | N/A
01/10/24 | TOC | Pass | N/A |  |  | N/A | N/A
01/10/24 | Particulate matter | Pass | N/A |  |  | N/A | N/A
01/10/24 | CO | Pass | N/A |  |  | N/A | N/A
01/10/24 | NH3 | Pass | N/A |  |  | N/A | N/A
01/10/24 | CO2 | Pass | N/A |  |  | N/A | N/A
01/10/24 | N20 | Pass | N/A |  |  | N/A | N/A
01/10/24 | O2 | Pass | N/A |  |  | N/A | N/A
01/10/24 | Moisture | Pass | N/A |  |  | N/A | N/A
01/10/24 | Velocity | Pass | N/A |  |  | N/A | N/A
Line 2 Standby | Results of annual surveillance tests (ASTs) for continuous emissions monitors
Date | Monitor | Pass/fail | Root cause of failure |  |  | Date of QAL2 | Date new calibration function entered
01/10/24 | HCl | Pass | N/A |  |  | N/A | N/A
01/10/24 | SO2 | Fail | Contacted Envea to look into the settings to ensure all correct, checked previous QAL 3 to ensure span and drift were acceptable. Checked for leaks on the system and gas pressures were all ok. |  |  | 2025-01-07 | TBC
01/10/24 | NO | Pass | N/A |  |  | N/A | N/A
01/10/24 | NO2 | Pass | N/A |  |  | N/A | N/A
01/10/24 | TOC | Pass | N/A |  |  | N/A | N/A
01/10/24 | Particulate matter | Pass | N/A |  |  | N/A | N/A
01/10/24 | CO | Pass | N/A |  |  | N/A | N/A
01/10/24 | NH3 | Pass | N/A |  |  | N/A | N/A
01/10/24 | CO2 | Pass | N/A |  |  | N/A | N/A
01/10/24 | N20 | Pass | N/A |  |  | N/A | N/A
01/10/24 | O2 | Pass | N/A |  |  | N/A | N/A
01/10/24 | Moisture | Pass | N/A |  |  | N/A | N/A
01/10/24 | Velocity | Pass | N/A |  |  | N/A | N/A

## Perf. Form 1
2024 | Annual Reporting Performance Form 1
Permit EPR/SP3239FU |  |  |  |  | Operator: | enfinium Ferrybridge 1 Ltd
Facility: | Enfinium Ferrybridge 1 Limited |  |  |  | Form: | Performance 1
Reporting Period from: |  |  | 2024-01-01 |  | to: | 2024-12-31
2024 | Annual Reporting of Waste Disposal and Recovery
Waste Description |  | Disposal Route(s) |  | Disposal Tonnes |  | Recovery Tonnes |  | % / tonne of waste incinerated
1) Hazardous Wastes
APC Residues |  | D9, R5 |  | 10778.79 |  | 12645.32 |  | 3.596%
Bulk waste oil |  | R13 |  |  |  | 3.96 |  | 0.000608%
Oil contaminated solid waste |  | R13 |  |  |  | 12.22 |  | 0.001876%
Fluorescent tubes |  | R13 |  |  |  | 1 |  | 0.0001535%
Lab chemicals |  | R13 |  |  |  | 0.665 |  | 0.0001021%
Total Hazardous Waste |  |  |  | 10778.79 |  | 12663.165 |  | 3.599%
2) Non-Hazardous Wastes
IBA |  | R5 |  |  |  | 121724.11 |  | 18.69%
Ferrous Metal |  | R4 |  |  |  | 4371.2 |  | 0.6711%
Dry Mixed recyclables |  | R13 |  |  |  | 8.6 |  | 0.00132%
General waste |  | R13 |  |  |  | 28.7 |  | 0.004406%
Wood |  | R3 |  |  |  | 15.88 |  | 0.002438%
Rubble |  | R13 |  |  |  | 83.04 |  | 0.01275%
Aqueous waste |  | D08 |  | 885.25 |  |  |  | 0.1359%
Sewage |  | D08 |  | 259.28 |  |  |  | 0.03981%
Electrical components |  | R13 |  |  |  | 3.64 |  | 0.0005588%
Total Non-Hazardous Waste |  |  |  | 1144.53 |  | 126235.17 |  | 19.56%
TOTAL WASTE |  |  |  | 11923.32 |  | 138898.335 |  | 23.16%
Operator’s comments :
2024 | Annual Reporting of Water and Other Raw Material Usage
Raw Material |  |  |  | Usage |  | Unit | Specific Usage |  | Unit
Mains Water |  |  |  | 92370 |  | m3 | 0.14182 |  | m3/te
Total Water |  |  |  | 151612.39 |  | m3 | 0.23277 |  | m3/te
Urea / Ammonia |  |  |  | 35102.84 |  | kg | 0.053893 |  | kg/te
Activated Carbon |  |  |  | 171016 |  | kg | 0.26256 |  | kg/te
Lime / hydrated lime / Sodium Bicarb. |  |  |  | 10349703.89 |  | kg | 15.8898 |  | kg/te
Operator’s comments :
2024 | Annual Reporting of other performance indicators
Parameter |  | Results by Line
|  | A1 | A2 | A3 | A4 | A5 |  | Turbine 1 | Turbine 2
Operating hours for the year, hours |  | 7861 | 7979.4 |  |  |  |  | 8399.4
Number of periods of abnormal operation, qty. |  | 6 | 3
Cumulative hours of abnormal operation for this year, hours |  | 14 | 7.5
Operator’s comments :
All abnormal operation events occurred in Q1 due to the same cause which were blockages of the Carbon dosing system.
Signed: | Lee Leonards |  |  |  |  | Date: | 2025-01-14

## Energy Form 1
2024 | Annual Reporting of Energy Usage/Export
Permit EPR/SP3239FU |  |  | Operator: | enfinium Ferrybridge 1 Ltd
Facility: | Enfinium Ferrybridge 1 Limited |  | Form: | Energy 1
Reporting Period from: |  | 2024-01-01 | to: | 2024-12-31
Energy Source |  | Energy Usage | Unit | Specific Usage (KWh/tonne incinerated
Electricity Produced |  | 646294.58 | MWh | 992.2527
Electricity Imported |  | 674.99 | MWh | 1.0363
Electricity Exported |  | 587685 | MWh | 902.2697
Gas Oil |  | 848.37 | tonnes
Steam/hot water exported |  | 0 | GWh | -
Operator’s comments :
Review of Combined Heat and Power (CHP) options. It is a permit requirement that the viability of CHP implementation is reviewed at least every four years. Information submitted in the annual report for 2022 provides relevant information and there are no updates for 2024.
Signed: | Lee Leonards |  |  | Date: | 2025-01-14

## Permit Compliance
Annual Performance Report 2024 |  |  |  | Enfinium Ferrybridge 1 Limited
Summary of Permit Compliance
Compliance with permit limits for continuously monitored pollutants
The plant met its emission limits as shown in the table below:
Substance |  | Percentage time compliant during operationNote 1 | [6 empty] | Notes:
|  | Half-hourly limit |  |  | Daily limit |  |  |  | Note 1: Please report to 2 decimal places, i.e. xx.xx% Note 2: Please enter into this table any permit non-compliances that the EA has given a CCS score for. Please also enter any other non-compliances which you have notified to the EA (e.g. ELV exceedances) but which have not yet been assessed by the EA. There is no need to enter any notifications which were subsequently assessed by the EA not to be permit breaches. Note 3: Please enter information here (rather than just referencing the notifications that were sent to the EA) including where relevant the incineration line reference, pollutant and value of the measured result for any ELV exceedances.
Particulates |  | 100% |  |  | 100%
Oxides of nitrogen |  | 100% |  |  | 100%
Sulphur dioxide |  | 100% |  |  | 100%
Carbon monoxide |  | 100.00% 95% of 10-min averages |  |  | 100%
Total organic carbon |  | 100% |  |  | 100%
Hydrogen chloride |  | 100% |  |  | 100%
Ammonia |  | 100% |  |  | 100%
Summary of non-compliances under the permit Note 2
Date | Summary of non-compliance Note 3 |  | Reason |  |  | Measures taken to prevent reoccurrence | CCS score if applicable*
[7 empty] | Impact | Root cause
*If the Environment Agency (EA) has given a Compliance Classification Scheme (CCS) score due to a permit non-compliance it should be entered here (CCS4 = No impact; CCS3 = Minor impact; CCS2 = Significant impact; CCS1 = Major impact). If the EA has not yet assessed a non-compliance which you have notified to them, these columns should be left blank.
Summary of any complaints received and actions to taken to resolve them.
Date | Summary of complaint [including Line/Reference] |  |  | Reason (including whether substantiated by the operator or the EA) |  |  | Measures taken to prevent reoccurrence
2024-03-31 | Odour complaint from a local resident 400m away |  |  | Unsubstantiated due to wind direction data and odour checks log |  |  | Discussed at morning meeting. Frequent Odour monitoring checks
2024-04-04 | Odour complaint from a local resident |  |  | Unsubstantiated due to wind direction data and odour checks log |  |  | Discussed at morning meeting. Frequent Odour monitoring checks
2024-04-08 | Odour complaint and dust complaint from local resident |  |  | Unsubstantiated due to wind direction data and odour checks log. Dust generation is minimal on site and therefore unlikely to be due to Ferrybridge 1 site. |  |  | Discussed at morning meeting. Frequent Odour monitoring checks

## Improvements
Annual Performance Report 2024 | Enfinium Ferrybridge 1 Limited
Summary of Plant Improvements
Summary of any efficiency improvements that have been completed within the year.
Replacement of light fittings to energy efficient LEDs
Summary of any permit improvement conditions that have been completed within the year and the resulting environmental benefits.
None
Summary of any changes to the plant or operating techniques which required a variation to the permit and a summary of the resulting environmental impact.
None
Summary of any other improvements made to the plant or planned to be made and a summary of the resulting environmental benefits.
None

## Public Liasion
Annual Performance Report 2024 |  | Enfinium Ferrybridge 1 Limited
Details of Public & Stakeholder Liaison
Summary of events held during the reporting year.
Date | Description
2024-11-21 | Transport liaison group meeting held
2024-12-01 | Community liaison group meeting held
List of events planned for next year
Date | Description
June & December 2025 | Community liaison group meetings to continueat 6 monthly intervals through the year, dates to be confirmed.
April/October 2025 | Transport liaison group meetings to continue at regular intervals through the year, dates to be confirmed.
If you wish to be involved in the public liaison programme, please contact Philip Curds philip.curds@enfinium.co.uk

## CO2 N2O
Annual Performance Report 2024 |  | Enfinium Ferrybridge 1 Limited
Carbon dioxide emissions and biogenic content of waste inputs |  |  |  | Notes:
Carbon dioxide emissions (all types of plant)
| Annual mass of carbon dioxide released | tonnes | 760510.1738
| Annual mass of carbon dioxide released per tonne of waste burned | t CO2 / t waste | 1.17
| Annual mass of carbon dioxide released per MWh of energy exported | t CO2 / MWh export | 1.2941
| Description of how annual carbon dioxide mass emission has been calculated. See Note 1 | CEMS CO2% calculated via Annual mass emissions report and converted into kg |  | Note 1: All permits require operators to continuously monitor CO2 to EN14181 and flow to BS EN 16911-2 (unless otherwise agreed in writing). Operators must therefore use the results from these instruments to calculate their annual CO2 emissions. Where an operator does not have a flow meter calibrated to BS EN 16911-2, the averaged flow measurement from that year's periodic monitoring can be used instead. If the plant does not have calibrated CO2 CEMS, a suitably justified emissions factor can be used.
Nitrous oxide emissions (only plants which use ammonia or urea to abate NOx emissions)
| Annual mass emissions of nitrous oxide | tonnes N2O | 1.5834
| Description of how annual nitrous oxide mass emission has been calculated See Note 2 | CEMS data has been used to calculate the mass emissions |  | Note 2: All permits require operators to continuously monitor N2O to EN14181 and flow to BS EN 16911-2, unless otherwise agreed in writing. Operators must therefore use the results from these instruments to calculate their annual N2O emissions. Where an operator does not have a flow meter calibrated to BS EN 16911-2, the averaged flow measurement from periodic monitoring can be used instead. If the plant does not have calibrated N2O CEMS, data from periodic monitoring or a suitably justified emissions factor can be used instead.
Total annual carbon dioxide + nitrous oxide emissions. See Note 3. |  | tonnes CO2e | 760929.7748 | Note 3: Total annual carbon dioxide and nitrous oxide emissions reported as carbon dioxide equivalent where 1 tonne nitrous oxide is equivalent to 265 tonnes carbon dioxide.
Biogenic CO2 emissions (See Note 4) |  |  |  | Note 4: Only plants combusting residual municipal waste, refuse derived fuel or solid recovered fuel need complete this section.
| Percentage of total carbon dioxide emissions arising from biogenic waste | % | 52.4%
| No. of measurements undertaken | Number | 222
| Description of how percentage biogenic carbon dioxide emissions have been measured or calculated. See Note 5 | Calculated from lab analysis via a UKAS accredited method ISO 216:2021. |  | Note 5: The results from C14 sampling should be used if this is carried out at the plant (either via an installed sampler or from spot samples). Otherwise, as an approximation (and in lieu of any more accurate metrics which may be developed in future), the measured or estimated biogenic fraction by net calorific value (see Note 6) can be assumed to be the same as the biogenic CO2 fraction of the total CO2 emissions from the plant.
Biogenic fraction of waste feedstock (See Note 4)
| Yearly average biogenic percentage of the waste by net calorific value (NCV) | % | 52.5%
| Description of how biogenic percentage (by NCV) has been calculated or estimated. See Note 6 | From fuel model which takes weighbridge data and RDF test results sampled at source (calculated from lab analysis via a UKAS accredited method ISO 21644:2021), then weights each suppliers tonnage on a heat input basis. |  | Note 6: If C14 sampling is carried out at the plant, the methodology set out in the embedded document entitled "Renewable Energy Association Energy Content of Fuels - Description of Method" embedded below can be used to calculate the biogenic percentage by net calorific value. Otherwise, data from waste sampling or BIOMA software can be used; or if none of these are available, an estimated figure with justification or a figure assumed on the basis of up-to-date industry data can be used.
| Yearly average biogenic percentage of the waste by mass | % | 57.1%
| If waste sampling undertaken, no. of samples used to ascertain average biogenic percentages above | Number | 302
| Description of how biogenic percentage (by mass) has been calculated or estimated. See Note 7 | From fuel model which takes weighbridge data and RDF test results sampled at source (calculated from lab analysis via a UKAS accredited method ISO 21644:2021), then weights each suppliers tonnage on a heat input basis. |  | Note 7: Where available, data from waste sampling should be used; otherwise, an estimated figure with justification can be used, or a figure assumed on the basis of up-to-date industry data.
Comments:
The numbers for waste sampling and biogenic content are provisional and based on an incomplete dataset, as some data is still waiting to be received.

## Residue Quality
Annual Performance Report 2024 |  |  | Enfinium Ferrybridge 1 Limited
Residue Quality Monitoring Requirements
Summary of monitoring undertaken and compliance
Monthly IBA hazard assessments and annual full hazardous property assessments, quarterly IBA and APC residue compliance monitoring, annual characterisation of IBA and APC residue. Analysis and reporting carried out by WRc.
Commentary on any specific events
Date & Event | Description
October 2024 - IBA and APC Annual Characterisation Report | Results of the annual characterisation of IBA and APC residues from Ferrybridge 1, including a full hazardous property assessment of IBA as required by the ESA Protocol 2018.
Residue Quality Monitoring Results
Parameter (unit) | Limit* | Normal Operation
|  | Bottom ash |  | APC Residues
Loss on Ignition (average %) | <5% | 1.9775
Total Organic Carbon (average %) | <3% | 0.65
No. of Assessments Undertaken | --- | 24 |  | 4
No. of Hazardous Results | --- | 0
* The permit will specify a limit of either 5% loss on ignition or 3% total organic carbon. If both are measured anyway, please enter the results here, even where the limit does not apply.
Comments :

## Water
Annual Performance Report 2024 |  |  | Enfinium Ferrybridge 1 Limited
Emissions to Water
Summary of monitoring undertaken and compliance
Sampling and analysis of attenuation pond water is carried out periodically, testing for pH and conductivity, and checking the odour and appearance depending upon operational activity.
Commentary on any specific events
Date & Event | Description
None
Emissions to Water / Sewer
Parameter |  | Monitoring Frequency |  | Limit | Target | Max. | Average
No parameters set in permit |  | N/A |  | None | None | None | N/A

## Air (periodic)
Annual Performance Report 2024 |  |  | Enfinium Ferrybridge 1 Limited
Emissions to Air (periodically monitored)
Summary of monitoring undertaken, standards used and compliance | [5 empty] | Notes:
Periodic Monitoring carried out in accordance with permit requirements using test methods CEN TS 17340 for HF; BS EN 14385 for cadmium, thallium and metals; EN 13211 for mercury; BS EN 1948 for dioxins and furans and PCBs, BS ISO 11338 for PAHs. All emissions were within the Emission Limit Values. | [5 empty] | Template may require adjustment for any bespoke monitoring requirements of permit - please also check that all default ELV values, reference periods and the stated oxygen reference value match those for your plant, and edit if necessary!
Results of emissions to air that are periodically monitored - oxygen reference 11%
Substance | Ref. Period | Emission Limit Value |  | Average |  | User to add additional tables as necessary, depending on whether quarterly or bi-annual reporting is required for the compliance year
|  |  |  | A1 | A2
Hydrogen fluoride | 1 hr | 1 mg/m3 |  | 0.0585 | 0.0585
Cd and Tl and their compounds | 0.5-8hrs | 0.02 mg/m3 |  | 0.00265 | 0.001
Hg and its compounds | 0.5-8hrs | 0.02 mg/m3 |  | 0.00305 | 0.00135
Sb, As, Pb, Cr, Co, Cu, Mn, Ni, V and their compounds | 0.5-8hrs | 0.3 mg/m3 |  | 0.061 | 0.0215
Dioxins & Furans (I-TEQ) | 6-8hrs | 0.06 ng/m3 |  | 0.01605 | 0.017
PCBs (WHO-TEQ Humans / Mammals) | 6-8hrs | None set ng/m3 |  | 0.00335 | 0.0107
PCBs (WHO-TEQ Fish) | 6-8hrs | None set ng/m3 |  | 0.000165 | 0.000103
PCBs (WHO-TEQ Birds) | 6-8hrs | None set ng/m3 |  | 0.0078 | 0.00525
Dioxins & Furans (WHO-TEQ Humans / Mammals) | 6-8hrs | None set ng/m3 |  | 0.01525 | 0.0155
Dioxins & Furans (WHO-TEQ Fish) | 6-8hrs | None set ng/m3 |  | 0.017 | 0.0098
Dioxins & Furans (WHO-TEQ Birds) | 6-8hrs | None set ng/m3 |  | 0.031 | 0.0275
Anthanthrene | 6-8hrs | None set µg/m3 |  | 0.0017 | 0.0019
Benzo(a)anthracene | 6-8hrs | None set µg/m3 |  | 0.052 | 0.0059
Benzo(a)pyrene | 6-8hrs | None set µg/m3 |  | 0.0017 | 0.0019
Benzo(b)fluoranthene | 6-8hrs | None set µg/m3 |  | 0.0028 | 0.0032
Benzo(b)naptho(2,1-d) thiophene | 6-8hrs | None set µg/m3 |  | 0.0017 | 0.002
Benzo(c)phenanthrene | 6-8hrs | None set µg/m3 |  | 0.0017 | 0.0019
Benzo(ghi)perylene | 6-8hrs | None set µg/m3 |  | 0.0034 | 0.0025
Benzo(k)fluoranthene | 6-8hrs | None set µg/m3 |  | 0.0017 | 0.0019
Cholanthrene | 6-8hrs | None set µg/m3 |  | 0.0017 | 0.0019
Chrysene | 6-8hrs | None set µg/m3 |  | 0.0074 | 0.0084
Cyclopenta(cd)pyrene | 6-8hrs | None set µg/m3 |  | 0.0017 | 0.0019
Dibenzo(ai)pyrene | 6-8hrs | None set µg/m3 |  | 0.0017 | 0.0019
Dibenzo(ah)anthracene | 6-8hrs | None set µg/m3 |  | 0.0017 | 0.0019
Fluoranthene | 6-8hrs | None set µg/m3 |  | 0.12 | 0.13
Indeno(123-cd) pyrene | 6-8hrs | None set µg/m3 |  | 0.0017 | 0.0019
Naphthalene | 6-8hrs | None set µg/m3 |  | 0.95 | 3.1
Comments :
All bi-annual and annual air emissions results are within the Emission limit values where applicable

## Air (CEMS)
Annual Performance Report 2024
Emissions to Air (continuously monitored)
Notes:
Summary of monitoring undertaken, standards used and compliance | [6 empty] | Template may require adjustment for any bespoke monitoring requirements of permit
Continuous emissions monitoring of Oxides of Nitrogen, Sulphur Dioxide, Hydrogen Chloride, Total Organic Carbon, Particulates, Ammonia and Carbon Monoxide (also Flow, O2, N2O) to EN14181. Instruments used PCME QAL 181, Oxymitter 4000, Envea MIR FT multigas analyser and Graphite 52M Flame Ionisation Detector (FID). All results demonstrate 100% compliance with the daily emission limit values. All results demonstrate 100% compliance with 1/2 hour average emission limit values. | [6 empty] | Please check that all default ELV values match those for your plant and edit if necessary!
Report to 1 decimal place
Results of emissions to air that are continuously monitored (maximum and average values for each line) - oxygen reference 11%
Substance | Reference Period | Emission Limit Value | A1 |  | A2
|  |  | Max. | Avg. | Max. | Avg.
Oxides of nitrogen | Daily mean | 180 mg/m3 | 170.23 | 154.64 | 164.69 | 149.24
| ½ hourly mean | 400 mg/m3 | 189 | 154.5 | 203 | 149.25
Particulates | Daily mean | 5 mg/m3 | 4.35 | 1.81 | 4.43 | 1.15
| ½ hourly mean | 30 mg/m3 | 17 | 1.75 | 24 | 1.25
Total Organic Carbon | Daily mean | 10 mg/m3 | 2.04 | 0.33 | 0.96 | 0.35
| ½ hourly mean | 20 mg/m3 | 10 | 0 | 6 | 0.25
Hydrogen chloride | Daily mean | 8 mg/m3 | 6 | 3.47 | 6.18 | 4.13
| ½ hourly mean | 60 mg/m3 | 30 | 3.5 | 15 | 4.25
Sulphur dioxide | Daily mean | 40 mg/m3 | 21.45 | 5.3 | 13.21 | 4.96
| ½ hourly mean | 200 mg/m3 | 103 | 5.42 | 50 | 5.08
Carbon monoxide | Daily mean | 50 mg/m3 | 42.18 | 11.52 | 19.78 | 9.11
| 95%ile 10-min avg * | 150 mg/m3 * | 69 | 11.5 | 73 | 9
Ammonia | Daily mean | 15 mg/m3 | 3.98 | 0.32 | 2.2 | 0.58
Comments :
No exceedances of emission limit values for any continuous emissions parameters

## HCl
Annual Performance Report 2024 |  |  |  | Enfinium Ferrybridge 1 Limited
Monitoring of Hydrogen Chloride emissions |  |  | Whole Installation |  |  | See Notes in Cell Q3 | Monitoring of Hydrogen Chloride emissions |  |  |  | Per Combustion Line |  | Notes:
User to add logic to complete Whole installation, Table A5:G18. From the data in Per Combustion Line, Table J6:O79, subject to No. of lines installed
2024 | 1/2 Hourly Reference Periods |  |  | Daily Reference Periods
mg/Nm3 | 1/2 hourly HCl ELV | Monthly mean of half-hourly averages | Highest half- hourly average | Daily HCl ELV | Monthly mean of daily averages | Highest daily average | 2024 | mg/Nm3 | Monthly mean of half-hourly averages | Highest half- hourly average | Monthly mean of daily averages | Highest daily average
Jan | 60 | 3.5 | 16 | 8 | 3.52 | 4.67 | A1 | Jan | 3 | 16 | 3.29 | 4.51
Feb | 60 | 4 | 30 | 8 | 3.905 | 5.78 |  | Feb | 4 | 30 | 3.83 | 5.78
Mar | 60 | 3 | 8 | 8 | 3.03 | 4.32 |  | Mar | 3 | 8 | 3.41 | 4.32 | Whole Installation table A5:G18:
Apr | 60 | 3 | 7 | 8 | 3.05 | 6.18 |  | Apr | 2 | 5 | 2.05 | 3.96 | Mean: for 1/2 hourly and daily periods calculate mean of values across all operational combustion lines for the month
May | 60 | 4.5 | 8 | 8 | 4.4 | 5.37 |  | May | 4 | 8 | 4.22 | 5.01
Jun | 60 | 4.5 | 8 | 8 | 4.41 | 5.99 |  | Jun | 4 | 8 | 4.23 | 5.22
Jul | 60 | 4 | 8 | 8 | 3.82 | 4.65 |  | Jul | 4 | 7 | 3.8 | 4.57 | Maximum: for 1/2 hourly and daily periods use the highest value across all operational combustion lines for the month
Aug | 60 | 4 | 14 | 8 | 4.05 | 5.75 |  | Aug | 4 | 14 | 3.65 | 4.5
Sep | 60 | 4 | 7 | 8 | 3.76 | 5.23 |  | Sep | 3 | 6 | 2.83 | 3.22
Oct | 60 | 4 | 8 | 8 | 4.01 | 5.74 |  | Oct | 3 | 6 | 3.05 | 3.89
Nov | 60 | 3.5 | 8 | 8 | 3.54 | 5.94 |  | Nov | 3 | 8 | 2.78 | 3.46
Dec | 60 | 4.5 | 15 | 8 | 4.115 | 6 |  | Dec | 5 | 13 | 4.52 | 6
[8 empty] | Annual | 3.5 | 30 | 3.4717 | 6
[7 empty] | 2024 | mg/Nm3 | Monthly mean of half-hourly averages | Highest half- hourly average | Monthly mean of daily averages | Highest daily average
[7 empty] | A2 | Jan | 4 | 8 | 3.75 | 4.67
[8 empty] | Feb | 4 | 8 | 3.98 | 4.92
[8 empty] | Mar | 3 | 8 | 2.65 | 3.82
[8 empty] | Apr | 4 | 7 | 4.05 | 6.18
[8 empty] | May | 5 | 7 | 4.58 | 5.37
[8 empty] | Jun | 5 | 8 | 4.59 | 5.99
[8 empty] | Jul | 4 | 8 | 3.84 | 4.65
[8 empty] | Aug | 4 | 11 | 4.45 | 5.75
[8 empty] | Sep | 5 | 7 | 4.69 | 5.23
[8 empty] | Oct | 5 | 8 | 4.97 | 5.74
[8 empty] | Nov | 4 | 7 | 4.3 | 5.94
[8 empty] | Dec | 4 | 15 | 3.71 | 4.99
[8 empty] | Annual | 4.25 | 15 | 4.13 | 6.18
Comments :

## SO2
Annual Performance Report 2024 |  |  |  | Enfinium Ferrybridge 1 Limited
Monitoring of Sulphur dioxide emissions |  |  | Whole Installation |  |  | See Notes in Cell Q3 | Monitoring of Sulphur dioxide emissions |  |  |  | Per Combustion Line |  | Notes:
User to add logic to complete Whole installation, Table A5:G18. From the data in Per Combustion Line, Table J6:O79, subject to No. of lines installed
2024 | 1/2 Hourly Reference Periods |  |  | Daily Reference Periods
mg/Nm3 | 1/2 hourly SO2 ELV | Monthly mean of half-hourly averages | Highest half- hourly average | Daily SO2 ELV | Monthly mean of daily averages | Highest daily average | 2024 | mg/Nm3 | Monthly mean of half-hourly averages | Highest half- hourly average | Monthly mean of daily averages | Highest daily average
Jan | 200 | 5 | 28 | 40 | 4.735 | 8.06 | A1 | Jan | 7 | 28 | 6.94 | 8.06
Feb | 200 | 5 | 103 | 40 | 5.105 | 11.95 |  | Feb | 8 | 103 | 7.76 | 11.95
Mar | 200 | 6 | 41 | 40 | 6.05 | 19.07 |  | Mar | 8 | 41 | 8.35 | 19.07 | Whole Installation table A5:G18:
Apr | 200 | 9.5 | 60 | 40 | 9.195 | 21.45 |  | Apr | 13 | 60 | 12.74 | 21.45 | Mean: for 1/2 hourly and daily periods calculate mean of values across all operational combustion lines for the month
May | 200 | 6 | 14 | 40 | 5.895 | 8.45 |  | May | 7 | 14 | 6.53 | 8.45
Jun | 200 | 4.5 | 11 | 40 | 4.525 | 6.51 |  | Jun | 3 | 11 | 3.11 | 3.86
Jul | 200 | 5 | 11 | 40 | 4.815 | 6.49 |  | Jul | 4 | 11 | 3.6 | 4.84 | Maximum: for 1/2 hourly and daily periods use the highest value across all operational combustion lines for the month
Aug | 200 | 4.5 | 29 | 40 | 4.555 | 6.25 |  | Aug | 3 | 29 | 3.21 | 3.74
Sep | 200 | 4.5 | 25 | 40 | 4.25 | 13.21 |  | Sep | 3 | 11 | 2.82 | 4.71
Oct | 200 | 4.5 | 15 | 40 | 4.09 | 6.42 |  | Oct | 3 | 15 | 2.65 | 3.68
Nov | 200 | 4 | 25 | 40 | 4.08 | 9.21 |  | Nov | 3 | 25 | 2.92 | 9.21
Dec | 200 | 4.5 | 50 | 40 | 4.255 | 8.18 |  | Dec | 3 | 35 | 2.94 | 5.85
[8 empty] | Annual | 5.4167 | 103 | 5.2975 | 21.45
[7 empty] | 2024 | mg/Nm3 | Monthly mean of half-hourly averages | Highest half- hourly average | Monthly mean of daily averages | Highest daily average
[7 empty] | A2 | Jan | 3 | 11 | 2.53 | 4.14
[8 empty] | Feb | 2 | 14 | 2.45 | 4.45
[8 empty] | Mar | 4 | 14 | 3.75 | 5.46
[8 empty] | Apr | 6 | 16 | 5.65 | 9.23
[8 empty] | May | 5 | 12 | 5.26 | 6.1
[8 empty] | Jun | 6 | 10 | 5.94 | 6.51
[8 empty] | Jul | 6 | 10 | 6.03 | 6.49
[8 empty] | Aug | 6 | 8 | 5.9 | 6.25
[8 empty] | Sep | 6 | 25 | 5.68 | 13.21
[8 empty] | Oct | 6 | 10 | 5.53 | 6.42
[8 empty] | Nov | 5 | 14 | 5.24 | 6.36
[8 empty] | Dec | 6 | 50 | 5.57 | 8.18
[8 empty] | Annual | 5.0833 | 50 | 4.9608 | 13.21
Comments :

## NOx
Annual Performance Report 2024 |  |  |  | Enfinium Ferrybridge 1 Limited
Monitoring of Oxides of Nitrogen emissions |  |  | Whole Installation |  |  | See Notes in Cell Q3 | Monitoring of Oxides of Nitrogen emissions |  |  |  | Per Combustion Line |  | Notes:
User to add logic to complete Whole installation, Table A5:G18. From the data in Per Combustion Line, Table J6:O79, subject to No. of lines installed
2024 | 1/2 Hourly Reference Periods |  |  | Daily Reference Periods
mg/Nm3 | 1/2 hourly NOx ELV | Monthly mean of half-hourly averages | Highest half- hourly average | Daily NOx ELV | Monthly mean of daily averages | Highest daily average | 2024 | mg/Nm3 | Monthly mean of half-hourly averages | Highest half- hourly average | Monthly mean of daily averages | Highest daily average
Jan | 400 | 151 | 203 | 180 | 151.1 | 162.06 | A1 | Jan | 151 | 180 | 150.75 | 162.06
Feb | 400 | 157.5 | 190 | 180 | 157.34 | 162.06 |  | Feb | 155 | 174 | 155.05 | 162.06
Mar | 400 | 148.5 | 190 | 180 | 148.425 | 160.83 |  | Mar | 148 | 176 | 148.11 | 160.83 | Whole Installation table A5:G18:
Apr | 400 | 146 | 170 | 180 | 146.02 | 152.62 |  | Apr | 147 | 170 | 147.41 | 152.34 | Mean: for 1/2 hourly and daily periods calculate mean of values across all operational combustion lines for the month
May | 400 | 148.5 | 181 | 180 | 148.27 | 170.23 |  | May | 156 | 181 | 155.82 | 170.23
Jun | 400 | 155 | 183 | 180 | 155.225 | 168.41 |  | Jun | 164 | 183 | 164.02 | 168.41
Jul | 400 | 155.5 | 180 | 180 | 155.755 | 168.24 |  | Jul | 159 | 180 | 159.47 | 168.24 | Maximum: for 1/2 hourly and daily periods use the highest value across all operational combustion lines for the month
Aug | 400 | 149 | 189 | 180 | 148.9 | 165.06 |  | Aug | 155 | 189 | 154.37 | 165.06
Sep | 400 | 143.5 | 177 | 180 | 143.72 | 161.07 |  | Sep | 150 | 177 | 150.4 | 161.07
Oct | 400 | 154.5 | 178 | 180 | 154.75 | 163.88 |  | Oct | 154 | 178 | 154.49 | 163.88
Nov | 400 | 156.5 | 187 | 180 | 156.85 | 164.64 |  | Nov | 154 | 187 | 154.66 | 164.45
Dec | 400 | 157 | 190 | 180 | 156.91 | 166.81 |  | Dec | 161 | 182 | 161.07 | 166.81
[8 empty] | Annual | 154.5 | 189 | 154.635 | 170.23
[7 empty] | 2024 | mg/Nm3 | Monthly mean of half-hourly averages | Highest half- hourly average | Monthly mean of daily averages | Highest daily average
[7 empty] | A2 | Jan | 151 | 203 | 151.45 | 159.48
[8 empty] | Feb | 160 | 190 | 159.63 | 161.88
[8 empty] | Mar | 149 | 190 | 148.74 | 160.73
[8 empty] | Apr | 145 | 167 | 144.63 | 152.62
[8 empty] | May | 141 | 168 | 140.72 | 147.11
[8 empty] | Jun | 146 | 170 | 146.43 | 154.06
[8 empty] | Jul | 152 | 175 | 152.04 | 157.21
[8 empty] | Aug | 143 | 167 | 143.43 | 153.22
[8 empty] | Sep | 137 | 176 | 137.04 | 154.91
[8 empty] | Oct | 155 | 173 | 155.01 | 161.46
[8 empty] | Nov | 159 | 173 | 159.04 | 164.64
[8 empty] | Dec | 153 | 190 | 152.75 | 164.69
[8 empty] | Annual | 149.25 | 203 | 149.2425 | 164.69
Comments :

## TOC
Annual Performance Report 2024 |  |  |  | Enfinium Ferrybridge 1 Limited
Monitoring of Total organic carbon emissions |  |  | Whole Installation |  |  | See Notes in Cell Q3 | Monitoring of Total organic carbon emissions |  |  |  | Per Combustion Line |  | Notes:
User to add logic to complete Whole installation, Table A5:G18. From the data in Per Combustion Line, Table J6:O79, subject to No. of lines installed
2024 | 1/2 Hourly Reference Periods |  |  | Daily Reference Periods
mg/Nm3 | 1/2 hourly TOC ELV | Monthly mean of half-hourly averages | Highest half- hourly average | Daily TOC ELV | Monthly mean of daily averages | Highest daily average | 2024 | mg/Nm3 | Monthly mean of half-hourly averages | Highest half- hourly average | Monthly mean of daily averages | Highest daily average
Jan | 20 | 0.5 | 4 | 10 | 0.6 | 0.96 | A1 | Jan | 0 | 2 | 0.49 | 0.79
Feb | 20 | 0.5 | 10 | 10 | 0.58 | 0.9 |  | Feb | 0 | 10 | 0.49 | 0.9
Mar | 20 | 0 | 8 | 10 | 0.41 | 2.04 |  | Mar | 0 | 8 | 0.39 | 2.04 | Whole Installation table A5:G18:
Apr | 20 | 0 | 2 | 10 | 0.295 | 0.86 |  | Apr | 0 | 2 | 0.3 | 0.86 | Mean: for 1/2 hourly and daily periods calculate mean of values across all operational combustion lines for the month
May | 20 | 0 | 6 | 10 | 0.23 | 0.5 |  | May | 0 | 3 | 0.19 | 0.31
Jun | 20 | 0.5 | 8 | 10 | 0.245 | 0.4 |  | Jun | 0 | 8 | 0.23 | 0.38
Jul | 20 | 0 | 3 | 10 | 0.3 | 0.43 |  | Jul | 0 | 3 | 0.33 | 0.43 | Maximum: for 1/2 hourly and daily periods use the highest value across all operational combustion lines for the month
Aug | 20 | 0 | 3 | 10 | 0.315 | 0.49 |  | Aug | 0 | 3 | 0.37 | 0.49
Sep | 20 | 0 | 3 | 10 | 0.32 | 0.5 |  | Sep | 0 | 3 | 0.37 | 0.5
Oct | 20 | 0 | 3 | 10 | 0.29 | 0.43 |  | Oct | 0 | 3 | 0.34 | 0.43
Nov | 20 | 0 | 3 | 10 | 0.24 | 0.36 |  | Nov | 0 | 3 | 0.23 | 0.35
Dec | 20 | 0 | 3 | 10 | 0.255 | 0.58 |  | Dec | 0 | 3 | 0.26 | 0.58
[8 empty] | Annual | 0 | 10 | 0.3325 | 2.04
[7 empty] | 2024 | mg/Nm3 | Monthly mean of half-hourly averages | Highest half- hourly average | Monthly mean of daily averages | Highest daily average
[7 empty] | A2 | Jan | 1 | 4 | 0.71 | 0.96
[8 empty] | Feb | 1 | 2 | 0.67 | 0.75
[8 empty] | Mar | 0 | 3 | 0.43 | 0.74
[8 empty] | Apr | 0 | 1 | 0.29 | 0.41
[8 empty] | May | 0 | 6 | 0.27 | 0.5
[8 empty] | Jun | 1 | 2 | 0.26 | 0.4
[8 empty] | Jul | 0 | 2 | 0.27 | 0.35
[8 empty] | Aug | 0 | 2 | 0.26 | 0.36
[8 empty] | Sep | 0 | 2 | 0.27 | 0.37
[8 empty] | Oct | 0 | 2 | 0.24 | 0.32
[8 empty] | Nov | 0 | 2 | 0.25 | 0.36
[8 empty] | Dec | 0 | 3 | 0.25 | 0.35
[8 empty] | Annual | 0.25 | 6 | 0.3475 | 0.96
Comments :

## Particulates
Annual Performance Report 2024 |  |  |  | Enfinium Ferrybridge 1 Limited
Monitoring of Particulate matter emissions |  |  | Whole Installation |  |  | See Notes in Cell Q3 | Monitoring of Particulate matter emissions |  |  |  | Per Combustion Line |  | Notes:
2024 | 1/2 Hourly Reference Periods |  |  | Daily Reference Periods | [8 empty] | User to add logic to complete Whole installation, Table A5:G18. From the data in Per Combustion Line, Table J6:O79, subject to No. of lines installed
mg/Nm3 | 1/2 hourly PM ELV | Monthly mean of half-hourly averages | Highest half- hourly average | Daily PM ELV | Monthly mean of daily averages | Highest daily average | 2024 | mg/Nm3 | Monthly mean of half-hourly averages | Highest half- hourly average | Monthly mean of daily averages | Highest daily average
Jan | 30 | 2 | 10 | 5 | 2.01 | 4.43 | A1 | Jan | 1 | 6 | 1.39 | 2.8
Feb | 30 | 2 | 6 | 5 | 1.75 | 2.67 |  | Feb | 2 | 4 | 1.61 | 2.48
Mar | 30 | 2.5 | 7 | 5 | 2.455 | 4.35 |  | Mar | 2 | 7 | 1.91 | 4.35
Apr | 30 | 0.5 | 4 | 5 | 1.065 | 2.3 |  | Apr | 1 | 3 | 1.4 | 1.82 | Whole Installation table A5:G18:
May | 30 | 1 | 4 | 5 | 0.655 | 1.69 |  | May | 1 | 4 | 1.1 | 1.69 | Mean: for 1/2 hourly and daily periods calculate mean of values across all operational combustion lines for the month
Jun | 30 | 1.5 | 14 | 5 | 1.235 | 2.87 |  | Jun | 2 | 5 | 1.87 | 2.87
Jul | 30 | 1.5 | 24 | 5 | 1.515 | 2.95 |  | Jul | 2 | 17 | 1.68 | 2.95
Aug | 30 | 1.5 | 7 | 5 | 1.72 | 3.04 |  | Aug | 2 | 7 | 2.19 | 3.04 | Maximum: for 1/2 hourly and daily periods use the highest value across all operational combustion lines for the month
Sep | 30 | 1.5 | 6 | 5 | 1.53 | 3.86 |  | Sep | 2 | 6 | 2.46 | 3.86
Oct | 30 | 1 | 4 | 5 | 1.41 | 3.18 |  | Oct | 2 | 4 | 2.45 | 3.18
Nov | 30 | 2 | 6 | 5 | 1.635 | 3.74 |  | Nov | 3 | 6 | 2.69 | 3.74
Dec | 30 | 1 | 6 | 5 | 0.75 | 1.76 |  | Dec | 1 | 3 | 0.91 | 1.76
[8 empty] | Annual | 1.75 | 17 | 1.805 | 4.35
[7 empty] | 2024 | mg/Nm3 | Monthly mean of half-hourly averages | Highest half- hourly average | Monthly mean of daily averages | Highest daily average
[7 empty] | A2 | Jan | 3 | 10 | 2.63 | 4.43
[8 empty] | Feb | 2 | 6 | 1.89 | 2.67
[8 empty] | Mar | 3 | 6 | 3 | 3.86
[8 empty] | Apr | 0 | 4 | 0.73 | 2.3
[8 empty] | May | 1 | 1 | 0.21 | 0.33
[8 empty] | Jun | 1 | 14 | 0.6 | 1.65
[8 empty] | Jul | 1 | 24 | 1.35 | 2.64
[8 empty] | Aug | 1 | 4 | 1.25 | 2.71
[8 empty] | Sep | 1 | 2 | 0.6 | 0.74
[8 empty] | Oct | 0 | 1 | 0.37 | 0.52
[8 empty] | Nov | 1 | 2 | 0.58 | 0.85
[8 empty] | Dec | 1 | 6 | 0.59 | 1.43
[8 empty] | Annual | 1.25 | 24 | 1.15 | 4.43
Comments :

## CO 0.5 hourly
Annual Performance Report 2024 |  |  |  | Enfinium Ferrybridge 1 Limited
Monitoring of Carbon Monoxide (half hourly) |  |  | Whole Installation |  |  | See Notes in Cell Q3 | Monitoring of Carbon Monoxide (half hourly) |  |  |  | Per Combustion Line |  | Notes:
Please complete this tab for your plant if you have 1/2 hourly CO ELVs; otherwise, leave it blank and complete the CO 95% 10 min tab | [12 empty] | User to add logic to complete Whole installation, Table A5:G18. From the data in Per Combustion Line, Table J6:O79, subject to No. of lines installed
[7 empty] | 2024 | mg/Nm3 | Monthly mean of half-hourly averages | Highest half- hourly average | Monthly mean of daily averages | Highest daily average
[7 empty] | A1 | Jan
2024 | 1/2 Hourly Reference Periods |  |  | Daily Reference Periods |  |  |  | Feb
mg/Nm3 | 1/2 hourly CO ELV | Monthly mean of half-hourly averages | Highest half- hourly average | Daily CO ELV | Monthly mean of daily averages | Highest daily average |  | Mar
Jan | 100 |  |  | 50 |  |  |  | Apr |  |  |  |  | Whole Installation table A5:G18:
Feb | 100 |  |  | 50 |  |  |  | May |  |  |  |  | Mean: for 1/2 hourly and daily periods calculate mean of values across all operational combustion lines for the month
Mar | 100 |  |  | 50 |  |  |  | Jun
Apr | 100 |  |  | 50 |  |  |  | Jul
May | 100 |  |  | 50 |  |  |  | Aug |  |  |  |  | Maximum: for 1/2 hourly and daily periods use the highest value across all operational combustion lines for the month
Jun | 100 |  |  | 50 |  |  |  | Sep
Jul | 100 |  |  | 50 |  |  |  | Oct
Aug | 100 |  |  | 50 |  |  |  | Nov
Sep | 100 |  |  | 50 |  |  |  | Dec
Oct | 100 |  |  | 50 |  |  |  | Annual | #DIV/0! | 0 | #DIV/0! | 0
Nov | 100 |  |  | 50
Dec | 100 |  |  | 50 |  |  | 2024 | mg/Nm3 | Monthly mean of half-hourly averages | Highest half- hourly average | Monthly mean of daily averages | Highest daily average
[7 empty] | A2 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2024 | mg/Nm3 | Monthly mean of half-hourly averages | Highest half- hourly average | Monthly mean of daily averages | Highest daily average
[7 empty] | A3 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
Comments : | [6 empty] | 2024 | mg/Nm3 | Monthly mean of half-hourly averages | Highest half- hourly average | Monthly mean of daily averages | Highest daily average
[7 empty] | A4 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2024 | mg/Nm3 | Monthly mean of half-hourly averages | Highest half- hourly average | Monthly mean of daily averages | Highest daily average
[7 empty] | A5 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0

## CO 95% 10 min
Annual Performance Report 2024 |  |  |  | Enfinium Ferrybridge 1 Limited
Monitoring of Carbon Monoxide (10-minute avg) |  |  |  | Whole Installation |  |  | See Notes in Cell S3 | Monitoring of Carbon Monoxide (10-minute avg) |  |  |  |  | Per Combustion Line |  | Notes: | Notes:
Please complete this tab for your plant if you have 10-minute average CO ELVs; otherwise, leave it blank and complete the CO 0.5 hourly tab
User to add logic to complete Whole installation, Table A5:H18. From the data in Per Combustion Line, Table K6:Q79, subject to No. of lines installed
2024 | 10-minute Reference Periods |  |  |  | Daily Reference Periods
mg/Nm3 | 95%ile 10-min avg CO ELV | Highest daily 95%ile 10-min average | Monthly mean of 10-min averages | Highest 10-min average | Daily CO ELV | Monthly mean of daily averages | Highest daily average |  | 2024 | mg/Nm3 | Highest daily 95%ile 10-min average | Monthly mean of 10-min averages | Highest 10-min average | Monthly mean of daily averages | Highest daily average
Jan | 150 | 23 | 6.5 | 526 | 50 | 6.185 | 7.65 |  | A1 | Jan | 21 | 8 | 242 | 7.65 | 10.46
Feb | 150 | 31 | 7 | 1595 | 50 | 7.47 | 9.73 |  |  | Feb | 31 | 9 | 1595 | 9.73 | 42.18
Mar | 150 | 43 | 8.5 | 423 | 50 | 8.645 | 10.53 |  |  | Mar | 43 | 10 | 423 | 10.53 | 37.18 | Whole Installation table A5:H18:
Apr | 150 | 73 | 9.5 | 193 | 50 | 9.87 | 10.18 |  |  | Apr | 61 | 10 | 164 | 10.18 | 11.72 | Mean: for 10-min and daily periods use average of all operational combustion lines.
May | 150 | 24 | 9 | 300 | 50 | 9.225 | 10.43 |  |  | May | 22 | 8 | 300 | 8.02 | 11.77
Jun | 150 | 19 | 9 | 491 | 50 | 9.12 | 10.28 |  |  | Jun | 13 | 8 | 491 | 7.96 | 12.43
Jul | 150 | 28 | 9.5 | 328 | 50 | 9.455 | 10.15 |  |  | Jul | 28 | 9 | 328 | 8.76 | 12.95 | Maximum: for 10-min and daily periods use the highest of all operational combustion lines in any month.
Aug | 150 | 58 | 13.5 | 451 | 50 | 13.685 | 15.99 |  |  | Aug | 58 | 16 | 451 | 15.99 | 24.87
Sep | 150 | 69 | 15 | 306 | 50 | 15.005 | 17.62 |  |  | Sep | 69 | 18 | 306 | 17.62 | 27.52
Oct | 150 | 50 | 12 | 338 | 50 | 11.77 | 13.65 |  |  | Oct | 50 | 14 | 338 | 13.65 | 20.43
Nov | 150 | 68 | 13 | 589 | 50 | 12.895 | 17.15 |  |  | Nov | 68 | 17 | 589 | 17.15 | 28.94
Dec | 150 | 27 | 10.5 | 921 | 50 | 10.45 | 10.98 |  |  | Dec | 27 | 11 | 343 | 10.98 | 22.55
[10 empty] | Annual | 40.9167 | 11.5 | 1595 | 11.5183 | 42.18
[9 empty] | 2024 | mg/Nm3 | Highest daily 95%ile 10-min average | Monthly mean of 10-min averages | Highest 10-min average | Monthly mean of daily averages | Highest daily average
[9 empty] | A2 | Jan | 23 | 5 | 526 | 4.72 | 13.11
[10 empty] | Feb | 27 | 5 | 252 | 5.21 | 10.59
[10 empty] | Mar | 18 | 7 | 193 | 6.76 | 10.41
[10 empty] | Apr | 73 | 9 | 193 | 9.56 | 16.13
[10 empty] | May | 24 | 10 | 158 | 10.43 | 15.18
[10 empty] | Jun | 19 | 10 | 190 | 10.28 | 13.33
[10 empty] | Jul | 17 | 10 | 187 | 10.15 | 12.38
[10 empty] | Aug | 20 | 11 | 234 | 11.38 | 14.35
[10 empty] | Sep | 48 | 12 | 304 | 12.39 | 19.78
[10 empty] | Oct | 17 | 10 | 177 | 9.89 | 11.77
[10 empty] | Nov | 15 | 9 | 162 | 8.64 | 12.11
[10 empty] | Dec | 25 | 10 | 921 | 9.92 | 18.55
[10 empty] | Annual | 27.1667 | 9 | 921 | 9.1108 | 19.78
Comments :
Environment Agency explanatory note: The 10-minute average ELV is based on the “95th percentile”. In this case this means that 95% of the 10 minute averages in the relevant 24-hour period (i.e. 137) must be below 150 mg/Nm3, and 5% (i.e. 7) are allowed to be any value above 150 mg/Nm3. Whilst we expect operators to minimise CO emissions at all times, it is perfectly acceptable for the value of the maximum 10-minute average to be above 150 mg/Nm3, provided the 95th percentile ELV has been met for that period.

## NH3
Annual Performance Report 2024 |  |  |  | Enfinium Ferrybridge 1 Limited
Monitoring of Ammnonia emissions |  |  | Whole Installation |  |  | See Notes in Cell Q3 | Monitoring of Ammnonia emissions |  |  |  | Per Combustion Line |  | Notes:
User to add logic to complete Whole installation, Table A5:G18. From the data in Per Combustion Line, Table J6:O79, subject to No. of lines installed
2024 | 1/2 Hourly Reference Periods |  |  | Daily Reference Periods
mg/Nm3 | 1/2 hourly NH3 ELV | Monthly mean of half-hourly averages | Highest half- hourly average | Daily NH3 ELV | Monthly mean of daily averages | Highest daily average | 2024 | mg/Nm3 | Monthly mean of half-hourly averages | Highest half- hourly average | Monthly mean of daily averages | Highest daily average
Jan | None | 0 | 4 | 15 | 0.2 | 0.46 | A1 | Jan | 0 | 4 | 0.13 | 0.41
Feb | None | 0 | 1 | 15 | 0.175 | 0.36 |  | Feb | 0 | 1 | 0.12 | 0.36
Mar | None | 0 | 7 | 15 | 0.455 | 3.98 |  | Mar | 0 | 7 | 0.44 | 3.98 | Whole Installation table A5:G18:
Apr | None | 0.5 | 2 | 15 | 0.605 | 1.06 |  | Apr | 0 | 2 | 0.49 | 1.06 | Mean: for 1/2 hourly and daily periods calculate mean of values across all operational combustion lines for the month
May | None | 0.5 | 13 | 15 | 0.525 | 2.2 |  | May | 0 | 0 | 0.34 | 0.39
Jun | None | 0.5 | 1 | 15 | 0.48 | 0.77 |  | Jun | 0 | 1 | 0.31 | 0.36
Jul | None | 0.5 | 1 | 15 | 0.47 | 0.7 |  | Jul | 0 | 1 | 0.3 | 0.4 | Maximum: for 1/2 hourly and daily periods use the highest value across all operational combustion lines for the month
Aug | None | 0.5 | 2 | 15 | 0.49 | 0.77 |  | Aug | 0 | 1 | 0.34 | 0.47
Sep | None | 0.5 | 1 | 15 | 0.53 | 0.87 |  | Sep | 0 | 1 | 0.38 | 0.64
Oct | None | 0.5 | 1 | 15 | 0.46 | 0.65 |  | Oct | 0 | 1 | 0.31 | 0.37
Nov | None | 0.5 | 2 | 15 | 0.475 | 0.66 |  | Nov | 0 | 2 | 0.33 | 0.56
Dec | None | 0.5 | 5 | 15 | 0.535 | 1.66 |  | Dec | 0 | 2 | 0.33 | 0.61
[8 empty] | Annual | 0 | 7 | 0.31833 | 3.98
[7 empty] | 2024 | mg/Nm3 | Monthly mean of half-hourly averages | Highest half- hourly average | Monthly mean of daily averages | Highest daily average
[7 empty] | A2 | Jan | 0 | 1 | 0.27 | 0.46
[8 empty] | Feb | 0 | 1 | 0.23 | 0.35
[8 empty] | Mar | 0 | 1 | 0.47 | 0.72
[8 empty] | Apr | 1 | 1 | 0.72 | 0.95
[8 empty] | May | 1 | 13 | 0.71 | 2.2
[8 empty] | Jun | 1 | 1 | 0.65 | 0.77
[8 empty] | Jul | 1 | 1 | 0.64 | 0.7
[8 empty] | Aug | 1 | 2 | 0.64 | 0.77
[8 empty] | Sep | 1 | 1 | 0.68 | 0.87
[8 empty] | Oct | 1 | 1 | 0.61 | 0.65
[8 empty] | Nov | 1 | 1 | 0.62 | 0.66
[8 empty] | Dec | 1 | 5 | 0.74 | 1.66
[8 empty] | Annual | 0.75 | 13 | 0.58167 | 2.2
Comments :
An indicated ELV value of zero in the table above means that no ammonia limit is/was set in the permit.

## Template changes log
Log of changes to template (Environment Agency use only)
Date | Description of change | New version number and date
2024-01-16 | Air (periodic) tab: corrected default O2 reference from 6 to 11% | Version 23.5a (for incinerators) - 16/01/2024
2024-09-23 | Air (periodic) tab: corrected symbol for Thallium to Tl
2024-09-23 | Air (periodic) tab: removed last year's references to different emission limit values applying from 03/12/23 and updated all relevant ELVs
2024-09-23 | Tabs for continuously monitored pollutants (HCl, SO2 etc.): changed terminology in table headings to improve clarity
2024-09-23 | Tabs for continuously monitored pollutants (HCl, SO2 etc.): removed last year's references to different emission limit values applying from 03/12/23 and updated all relevant ELVs
2024-09-23 | Perf 1 tab: updated formula for water usage to report m3 rather than litres and corrected error with formula copying operator name
2024-09-23 | Operational Summary tab: table added on start-up's and shut-downs
2024-09-23 | Operational Summary tab: table added on dioxins and mercury protocols
2024-09-23 | Operational Summary tab: table added on AST, QAL 2 and calibration functions
2024-09-23 | CO2 N2O tab: various changes made to notes to reflect the fact that most plants should now have calibrated CEMS and flow meters + some have C14 samplers and more up to date industry data | Version 24a (for incinerators) - 23/09/24
2024-01-08 | CO2 N2O tab: Changed the N2O CO2 equivalence factor from 298 to 265 in line with recently updated government greenhouse gas figures: https://www.gov.uk/government/publications/greenhouse-gas-reporting-conversion-factors-2024
2024-01-08 | CO2 N2O tab: Added an additional requirement for municipal EfW plants to state the yearly average biogenic percentage of the waste by mass, and reference to a document which sets out a methodology for calculating NCV of waste from the results of C14 sampling.
2024-01-08 | Permit Compliance tab: Two additional columns added + explanatory notes to the table entitled "Summary of non-compliances under the permit" to allow CCS scores to be stated where relevant.
2024-01-08 | Residue Quality tab: Note added explaining application of TOC and LOI limits and asking operators to report both metrics where measured. | Version 24.1a (for incinerators) - 08/11/24