## Cover Page
Version 20.1
Add photo
Notes:
This template may require adjustments by individual operators to meet specific reporting requirements as defined in the site Permit(s)
Annual Performance Report 2020
Permit No. P0446/14A/V1
Full Circle Generation Ltd
Energy From Waste Plant
Full Circle Generation Ltd
Year: | 2020
Address: | 7 Irwin Way, Airport Road West, Belfast, BT3 9ED
Tel:
Email:
Prepared by: | Alen Sarlah | Position: | Technical Manager (BYES)
Approved by: | Alan Cassells | Position: | Plant Manager (BYES)
Approved by: | Harry Lockhart | Position: | Senior General Manager (FCG)
Version: | 1
Issue Date: | 2021-03-03
Print Report
Print as PDF
GENERATION

## Contents
Annual Performance Report 2020 |  | Full Circle Generation Ltd
Contents |  |  |  | Notes:
Section | Subject |  | Page | Section references and Page nos. to be inserted
| Facility Information |  |  | Sections and Subjects may require adjustment by individual operators to meet specific reporting requirements as defined in the sites Permit(s)
Operational Summary
Operational Data
Performance Form 1
Energy Form 1
Permit Compliance
Improvements
Public Liasion
Residue Quality - Optional
Emissions to Water
Emissions to Air (periodically monitored)
Emissions to Air (continuously monitored)
Hydrogen Chloride emissions
Sulphur Dioxdie emsissions
Oxides of Notrigen emissions
Total Organic Carbon emissions
Particulate Matter emissions
Carbon Monoxide emissions
Ammonia emissions
Version Control
Section | Information |  | Date
1 | Preliminary |  | 2021-01-15
2 | Revised and updated |  | 2021-03-03
Distribution
Copy | Name, Role |  | No.
1 | Harry Lockhart, FCG - Senior General Manager
2 | Steven Castles, NIEA - Pollution Inspector
3 | BYES
This report is required under the Industrial Emissions Directive’s Article 55(2) requirements on reporting and public information on waste incineration plants and co-incineration plants, which require the operator to produce an annual report on the functioning and monitoring of the plant and make it available to the public.

## Facility Info
Annual Performance Report 2020 | Full Circle Generation Ltd
Plant Description and Design |  |  |  | Notes:
Plant is located in the industrial zone of Belfast docks, surrounded by Belfast City airport and Flogas. It has three lines, ie 3 off RDF gasifiers/boilers, each 20.8MW net thermal. Design throughput of each line is 5.4 t/h of RDF. Total of 16.2 t/h per plant. RDF NCV range: 11.5-16.5 MJ/kg. 2 steam turbines: 4.87 and 9.98MWe. Flue gas scrubbing system consists of SNCR (urea) and dry abatement (lime+PAC) with bag filters. |  |  |  | Include summary of plant design, design capacity, no. of combustion lines, electrical and heat capacity and any other general information that descibes the facility, its location and purpose
Summary of Operational Processes and Procedures
Plant has a long list of SOPs covering all areas of the plant including: - Waste reception, waste handling, waste quarantine, waste sampling - Residue handling, storage and transport - All process-related systems including for fuel metering, operation of gasifier, boiler, filtration, RDF and ash systems, water-steam cycle - Functional safety test procedures - Start up and shutdown procedures - Maintenance procedures - Building management procedures (housekeeping, safety checks, ...) - Statutorey inspections, tests and checking. - CEMS monitoring and calibration - H&S related procedures (dust emissions, safety tests, site access and inductions, training,...) Plant also has critical EOPs covering: - fire procedures - gas release procedure - grid blackout - neighbouring site emergency - boiler leak - liquid spillage - steam turbine emergency (fire plan, overspeed, oil leak, TX fire plan) All SOPs are regularly reviewed and updated. |  |  |  | Include summary of key processes and procedures such as (but not limited to); waste reception, control rooms, grate, bed and bolier, energy & heat generation, cooling systems, residue management, emission controls, health and safety systems, maintenance
Signed |  | Date | 2021-03-08

## Operational Data
Annual Performance Report 2020 |  |  |  | Full Circle Generation Ltd
Operational Data | [7 empty] | Notes:
Plant Size | 144000 |  | tonnes pa | 20.8 | MWth | 14.85 | MWe | * - RDF to include SRF
No. of combustion lines | 3 |  | No. of Turbines: |  | 2 |  |  | ** - CHP plants only
2020 updates include; heat in MWh, water in Litres, NCV in MJ/kg
Waste types received | Unit | Q1 | Q2 | Q3 | Q4 | Year Total | %
Household / Local Authority | tonnes |  |  |  |  | 0 | - | Availability Definition: 'the availability of a line is to be calculated by the number of hours the line reported Continuously Monitored emission levels to the Regulator through the calendar year divided by the total number of hours in that year. The overall plant availability is calculated as the Mean of all lines in the plant. For clarity this includes periods of Other Than Normal Operating Conditions (OTNOC) and abnormal operation.' Rationale: The primary function of an Energy from Waste facility is the disposal of waste. It follows therefore that the availability of a plant is determined by the period of time a facility spends undertaking this activity.
Commercial & Industrial | [5 empty] | 0 | -
Hazardous | [5 empty] | 0 | -
Clinical | [5 empty] | 0 | -
Waste wood (biomass) | [5 empty] | 0 | -
Refuse Derived Fuel * - H'hold/LA |  | 21751.64 | 29826.13 | 18802.89 | 6014 | 76394.66 | 100%
Refuse Derived Fuel * - C&I | [5 empty] | 0 | -
Other [Please specify] | [5 empty] | 0 | -
Other [Please specify]
Other [Please specify]
Total waste combusted |  | 21751.64 | 29826.13 | 18802.89 | 6014 | 76394.66 | 100%
Rejected Waste | [5 empty] | 0 | -
Unprocessed waste transferred out | [5 empty] | 0 | -
Energy Useage / Export | Unit | Q1 | Q2 | Q3 | Q4 | Year Total | KWh/te
Power Generated | MWh | 13089.019 | 20135.242 | 11216.567 | 4463.295 | 48904.123 | 640.1511
Power Exported |  | 10570.416 | 16082.073 | 8996.674 | 3708.75 | 39357.913 | 515.1919
Power Used on site | [5 empty] | 0 | -
Power Imported |  | 478.314 | 97.397 | 583.414 | 596.651 | 1755.776 | 22.983
Parasitic Load | % | 22.09% | 20.51% | 23.76% | 26.7% | 22.31%
Thermal Energy Produced ** | MWh |  |  |  |  | 0 | -
Thermal Energy Exported ** | [5 empty] | 0 | -
R1 value |  | 0.74 |  |  |  | Design
Waste Disposal & Recovery | Unit | Q1 | Q2 | Q3 | Q4 | Year Total | % inputs
APC Residues - produced | tonnes | 918.25 | 1167.35 | 737.15 | 319.86 | 3142.61 | 4.114%
IBA - produced |  | 2511.5 | 3558.8 | 1872.6 | 698.9 | 8641.8 | 11.31%
Metals recycling | [5 empty] | 0 | -
Boiler Ash |  | 131.92 | 115.8 | 106.731 | 80.4 | 434.851 | 0.5692%
UGC Ash |  | 567.06 | 873.4 | 461.28 | 191.8 | 2093.54 | 2.74%
Other Hazardous Waste (Filter Bags) |  | 0 | 0 | 21.78 | 0 | 21.78 | 0.02851%
Raw Material Usage | Unit | Q1 | Q2 | Q3 | Q4 | Year Total | kg or Ltr /te
Mains Water | ltrs | 13300 | 13600 | 11942 | 3285 | 42127 | 0.55144
Other Water | ltrs |  |  |  |  | 0 | -
Ammonia | kgs |  |  |  |  | 0 | -
Urea (32% solution) | Ltrs | 33937 | 23039 | 10916 | 3792 | 71684 | 0.93834
Activated Carbon | kgs | 15500 | 22000 | 15000 | 7000 | 59500 | 0.77885
Lime / hydrated lime | kgs | 276156 | 425199 | 310780 | 146300 | 1158435 | 15.1638
Fuel oil | ltrs | 210 | 1464 | 13510 | 9390 | 24574 | 0.32167
Gas | M3 | 406604 | 186831 | 220648 | 13480 | 827563
Other |  | 0 | 0 | 0 | 0 | 0
Summary | Line/Unit | Q1 | Q2 | Q3 | Q4 | Year Total
Availability of waste combustion by line, hrs | 1 | 1055 | 1953.8 | 913.2 | 386.2 | 4308.2 | #REF!
| 2 | 1540.2 | 1456.4 | 1026.9 | 376.2 | 4399.7 | #REF!
| 3 | 1453 | 1883.8 | 1201.5 | 457.6 | 4995.9 | #REF!
| 4 | - | - | - |  | 0 | x %
| 5 | - | - | - |  | 0 | x %
Overall Availability, mean avg. of all lines, hrs |  | 1349.4 | 1764.6667 | 1047.2 | 406.6667 | 2740.76 | x %
Hours of turbine operations, hrs | 1 | 1595 | 2158 | 1050 | 457 | 5260 | x %
Hours of turbine operations, hrs | 2 | 1330 | 1881 | 1155 | 349 | 4715 | x %
Hours of heat / steam export |  | 0 | 0 | 0 | 0 | 0 | n/a
Net Calorific Value of waste | MJ/kg | 14.1 | 16.2 | 16.2 | 12.5 | 14.75 | -
Abnormal Events | qty. | 0 | 0 | 2 | 0 | 2 | yes
Abnormal operation | hours | 0 | 0 | 2 | 0 | 2 | #REF!
Permit Breaches | qty. | 17 | 8 | 2 | 1 | 28 | yes
Signed |  |  |  |  | Date | 2021-03-08

## Operational Summary
Annual Performance Report 2020 | Full Circle Generation Ltd
Summary of Plant Operations and Maintenance during the reporting year |  |  |  | Notes:
The Plant is undergoing performance testing and optimisation. There were 2 outages in the period. 1st was a Statutory outage – July/Aug and the 2nd was a Service and Inspection outage for turbines Nov/Dec. |  |  |  | Include summary of key operational and/or mainteanance activity undertaken in the year, such as any major component upgrades and/or replacements
Summary of Residue Handling for the reporting year
There are 4 residue sources at the plant: - IBA (Incineration Bottom Ash) from the end of the grate. Non-Haz. - UGC (Undergrate and Combustor ash). Haz. - Boiler ash. Haz. - APCr filter ash. Haz. Tonnages are indicated on previous page. IBA is collected in a common silo (from all three boilers), and discharged on trailers (covered) and taken to Riverridge site at Craigmore where it goes through a wash plant and is recovered for use as an aggregate. UGC is collected in big bags (separately from each stream), collected over teh month and transported off site regularly and disposed of to landfill at Augean's site at Port Clarence at Teesside. Boiler ash is collected in big bags (separately from each stream), collected over the month and transported off site regularly and disposed of to landfill at OCO's Wingmoor Farm site near Avonmouth. APCr filter ash is collected in two silos (from all three boilers), and discharged in tankers and and transported to OCO's facilty at Leeds and is recovered for use in the manufacture of concrete blocks |  |  |  | Include in here a summary of residue handling regimes and destinations
Signed |  | Date | 2021-03-08

## Perf. Form 1
2020 | Annual Reporting Performance Form 1
Permit No. P0446/14A/V1 |  |  |  |  | Operator: | 0
Facility: | Full Circle Generation Ltd |  |  |  | Form: | Performance 1
Reporting Period from: |  |  | 2020-01-01 |  | to: | 2020-12-31
2020 | Annual Reporting of Waste Disposal and Recovery
Waste Description |  | Disposal Route(s) |  | Disposal Tonnes |  | Recovery Tonnes |  | % / tonne of waste incinerated
1) Hazardous Wastes
APC Residues |  | OCO |  |  |  | 3142.6 |  | 4.114%
IBA | [7 empty] | -
UGC |  | RRR/Augean |  | 2093.54 |  |  |  | 2.74%
Boiler |  | OCO |  | 434.851 |  |  |  | 0.5692%
APCR Bag Filter |  | Augean |  | 21.78 |  |  |  | 0.02851%
Total Hazardous Waste |  |  |  | 2550.171 |  | 3142.6 |  | 7.452%
2) Non-Hazardous Wastes
IBA |  | RRR |  |  |  | 8641.8 |  | 11.31%
Ferrous Metal | [7 empty] | -
Process Water |  | Effluent - Sewage |  | 28084.6667 |  |  |  | 36.76%
-
-
Total Non-Hazardous Waste |  |  |  | 28084.6667 |  | 8641.8 |  | 48.07%
TOTAL WASTE |  |  |  | 30634.8377 |  | 11784.4 |  | 55.53%
Operator’s comments :
2020 | Annual Reporting of Water and Other Raw Material Usage
Raw Material |  |  |  | Usage |  | Unit | Specific Useage |  | Unit
Mains Water |  |  |  | 42127 |  | m3 | 0.55144 |  | m3/te
Total Water |  |  |  | 42127 |  | m3 | 0.55144 |  | m3/te
Urea |  |  |  | 71684 |  | kg | 0.93834 |  | kg/te
Activated Carbon |  |  |  | 59500 |  | kg | 0.77885 |  | kg/te
Lime |  |  |  | 1158435 |  | kg | 15.1638 |  | kg/te
Operator’s comments :
2020 | Annual Reporting of other performance indicators
Parameter |  | Results by Line
|  | A1 | A2 | A3 | A4 | A5 |  | Turbine 1 | Turbine 2
Operating hours for the year, hours |  | 4308.2 | 4399.7 | 4995.9
Number of periods of abnormal operation, qty.
Cumulative hours of abnormal operation for this year, hours
Operator’s comments :
Signed: | [5 empty] | Date: | 2021-03-08

## Energy Form 1
2020 | Annual Reporting of Energy Usage/Export
Permit No. P0446/14A/V1 |  |  | Operator: | Full Circle Generation Ltd
Facility: | Full Circle Generation Ltd |  | Form: | Energy 1
Reporting Period from: |  | 2020-01-01 | to: | 2020-12-31
Energy Source |  | Energy Usage | Unit | Specific Useage (KWh/tonne incinerated
Electricity Produced |  | 48904.123 | MWh | 640.1511
Electricity Imported |  | 1755.776 | MWh | 22.983
Electricity Exported |  | 39357.913 | MWh | 515.1919
Natural gas |  | 827563 | Nm3 | 9126.1809
Steam/hot water exported |  | 0 | GWh | -
Operator’s comments :
Signed: |  |  |  | Date: | 8/3/21

## Permit Compliance
Annual Performance Report 2020 |  |  | Full Circle Generation Ltd
Summary of Permit Compliance
Compliance with permit limits for continuously monitored pollutants
The plant met its emission limits as shown in the table below:
Substance |  | Percentage time compliant during operation |  |  |  |  | Notes:
|  | *97% or 100% Half-hourly limit |  | Daily limit |  |  | Operator shall have no more than 3% to be compliant with 97% Half-hourly for the year. Report to 2 decimal places, i.e. xx.xx%.Please provide a brief summary of each notification or non-compliance in the table (rather than just referring to notifications that were sent to the Regulator).
Particulates |  | 100% |  | 100%
Oxides of nitrogen |  | 100% |  | 100%
Sulphur dioxide |  | 99.98% |  | 100%
Total organic carbon |  | 99.99% |  | 100%
Hydrogen chloride |  | 99.99% |  | 100%
Hydrogen fluoride |  | 100% |  | 100%
Carbon monoxide |  | 99.91% |  | 100%
Summary of any notifications or non-compliances under the permit
Date | Summary of notification or non-compliance [including Line/Reference] |  | Reason |  |  | Measures taken to prevent reoccurrence
| Refer to all Sch 1 in the Appendix. | [5 empty] | As instructed by S.Castles
Summary of any complaints received and actions to taken to resolve them.
Date | Summary of complaint [including Line/Reference] |  | Reason * |  |  | Measures taken to prevent reoccurrence
None
* including whether substantiated by the operator or the NIEA
Signed |  |  |  |  | 2021-03-08

## Improvements
Annual Performance Report 2020 | Full Circle Generation Ltd
Summary of Plant Improvements
Summary of any efficiency improvements that have been completed within the year.
1. Sumerged scraper enhancements to include sprocket modification, addition of slide valve to control tramp air ingress and dust carryover, bolting of wear plates for quicker maintenance turnaround, non-drive end sprocket modified to enhance reliability - enhanced performance. 2. Larger doors fitted to gasifier to provide safer, quicker access & egress to gasifier grate - improved H&S. 3. Additional temperature instruments installed to combustion chambers and various gas path locations - enhanced process control. 4. Push floor bunker floors lined with hardox to decrease friction/wear on bunker and enhance push floor performance, upgrades to ram support struts and structure, flow diverters removed - enhanced process operation. 5. Boiler chemical dosing mods to include DCS control/visibility & optimise maintainability of dosing pumps - enhanced performance. 6. Modifications to combustion ash discharge conveyor - increased MTBF on bearings & screw, reduced dust escape - enhanced performance. 7. New design of grate shoes to reduce amount of ash, aluminium and other debris falling into undergrate system, and reduce amount of fly ash - enhanced performance. 8. New design gasifier undergrate ash discharge screw to reduce time taken to replace - enhanced performance.
Summary of any permit improvement conditions that have been completed within the year and the resulting environmental benefits.
Mechanical upgrades: 1. Metering bin levelling screws modification – better levelling of the RDF across whole gasifier bed, less blockages in metering bin and therefore less process interruptions, lower emissions. 2. Combustion cylinders ash discharge pressure equalisation line installed – reduced/stopped dusting in case of process interruptions. Software upgrades – improvements for environmental benefits 1. Automatic shutdown sequence was optimised to reduce emission spike at the end despite the fact that this time period is not reportable. 2. Gasification air fans and O2 regulation was changed from fixed settings to dynamic based on the Calorific Value of the RDF - improved process control. 3. O2 controller and regulation is using secondary O2 instrument as a backup in case of deviation of the primary one - improved process safety and emissions. 4. Superheated steam temperature controller was made more robust, faster and more precise – reducing chances for plant trip due to high temperature spikes. 5. Boiler water conductivity (TDS) was changed from local regulation to the DSC overall logic. By doing this consumption of chemicals was reduced, surges of hot water discharges eliminated,… 6. ID max speed is now also part of the plant load regulation – reducing load if Fan is maxed out instead of tripping plant on high pressure.
Summary of any changes to the plant or operating techniques which required a variation to the permit and a summary of the resulting environmental impact.
None
Summary of any other improvements made to the plant or planned to be made and a summary of the resulting environmental benefits.
1. Addition of CEMS local instrument air dryer pipework - improved CEMS reliability. 2. Improved boiler cleaning systems/techniques - improved availability, reliability and reduced filter load on baghouse filter. 3. Improved boiler ash removal - improved availability, reliability.
Signed |  | Date | 2021-03-08

## Public Liasion
Annual Performance Report 2020 |  | Full Circle Generation Ltd
Details of Public & Stakeholder Liasion
Summary of events held during the reporting year.
Date | Description
List of events planned for next year
Date | Description
If you wish to be involved in the public liasion programme, please contact __hlockhart@equitix.co.uk_______________

## Residue Quality
Annual Performance Report 2020 |  |  | Full Circle Generation Ltd
Residue Quality Monitoring Requirements
Summary of monitoring undertaken and compliance
IBA ash underwent 12-week assessment - determined to be non-Haz, compliant with the Permit. Quality monitored monthly with lab samples. Reports all submitted promptly.
UGC and Boiler ash - determined to be Haz.
APCr ash - determined to be Haz. Two samples sent to the lab to assess composition and propose plant/process improvements. These were implemented.
Commentary on any specific events
Date & Event | Description
None.
Residue Quality Monitoring Results
Parameter (unit) | Limit | Normal Operation
|  | Bottom ash |  | APC Residues
Loss on Ignition (average %) | <5% | 3.2
Total Organic Carbon (average %) | <3% | 1.3
No. of Assessments Undertaken | --- | 12 (one per month) |  | All batches tested as received
No. of Hazardous Results | --- | 0
Comments :
All samples were shown to be non-Haz. 1 IBA sample was sent to additional in-vitro tests to establih new limit values on pH.
Signed |  |  | Date | 2021-03-08

## Water
Annual Performance Report 2020 |  |  | Full Circle Generation Ltd
Emissions to Water
Summary of monitoring undertaken and compliance
Emissions to Ground water: Sampling and analysing performed by external lab. 2 samples showed increased COD and BOD. Repeated sampling shown no excedances. All later samples compliant.
Emissions to Sewage: Online monitoring for pH, temp and flow as per permit. All on DCS. Everything compliant. Some problems with flow meter - potential upgrade looked at. Additional blowdown cooling added to help keep temperatures sufficiently low at all times.
Commentary on any specific events
Date & Event | Description
None
Emissions to Sewer
Parameter |  | Monitoring Frequency |  | Limit | Min | Max | Avg
BOD (ATU) |  | Quaterly |  |  | 2.2 | 16 | 6.06
COD (Total) |  | Quaterly |  | 500 | 25 | 64 | 31.5
pH |  | Quaterly |  | 5-10 | 7.33 | 9.05 | 8.12
Suspended Solids |  | Quaterly |  | 300 | 3 | 126 | 36.5
Temperature (Deg C) |  | Quaterly |  | <43 | 16.3 | 20.2 | 18.4
Visible Oil & Grease |  | Quaterly |  | None Visible | 1 | 1 | 1
Emissions to Water
Parameter |  | Monitoring Frequency |  | Limit | Min | Max | Avg
BOD (ATU) |  | Quaterly |  | 10 | 1.95 | 53.5 | 7.54
COD (Total) |  | Quaterly |  |  | <25 | 120 | 47
pH |  | Quaterly |  | 6-9 | 7.18 | 9.12 | 7.88
Suspended Solids |  | Quaterly |  | 50 | 13 | 24 | 23.2
Temperature |  | Quaterly |  | 25 | 16.1 | 20.3 | 18.3
Visible Oil & Grease |  | Quaterly |  | None Visible | 1 | 1 | 1
Signed |  |  |  | Date | 2021-03-08

## Air Q1 (periodic)
Annual Performance Report 2020 |  |  | Full Circle Generation Ltd
Emissions to Air (periodically monitored)
Summary of monitoring undertaken, standards used and compliance | [8 empty] | Notes:
A1 Testing Duration : 9th to 12th March 2020 A2 Testing Duration : 9th to 12th March 2020 A3 Testing Duration : 17th to 28th Feb 2020 | [8 empty] | Template may require adjustment for any bespoke monitoring requirements of permit.
Results of emissions to air that are periodically monitored
Substance | Ref. Period | Emission Limit Value |  | Average |  |  |  |  | User to add additional tables as necessary, depending on whether quarterly or bi-annual reporting is required for the compliance year
|  |  |  | A1 | A2 | A3 | A4 | A5
Hydrogen fluoride | 1 hr | 2 mg/m3 |  | 0.01 | 0.01 | 0.02 | - | -
Cd and Tl and their compounds | 6-8hrs | 0.05 mg/m3 |  | 0.0127 | 0.0077 | 0.0099 | - | -
Hg and its compounds | 6-8hrs | 0.05 mg/m3 |  | 0.0012 | 0.0009 | 0.0021 | - | -
Sb, As, Pb, Cr, Co, Cu, Mn, Ni, V and their compounds | 6-8hrs | 0.5 mg/m3 |  | - | - | - | - | -
Dioxins & Furans (I-TEQ) | 6-8hrs | 0.1 ng/m3 |  | 0.0465 | 0.0098 | 0.0785 | - | -
PCBs (WHO-TEQ Humans / Mammals) | 6-8hrs | None set ng/m3 |  | 0.0023 | 0.0004 | 0.0084 | - | -
PCBs (WHO-TEQ Fish) | 6-8hrs | None set ng/m3 |  | 0.0001 | 0 | 0.0004 | - | -
PCBs (WHO-TEQ Birds) | 6-8hrs | None set ng/m3 |  | 0.0032 | 0.0009 | 0.0149 | - | -
Dioxins & Furans (WHO-TEQ Humans / Mammals) | 6-8hrs | None set ng/m3 |  | 0.0419 | 0.0092 | 0.0721 | - | -
Dioxins & Furans (WHO-TEQ Fish) | 6-8hrs | None set ng/m3 |  | 0.0383 | 0.0085 | 0.0686 | - | -
Dioxins & Furans (WHO-TEQ Birds) | 6-8hrs | None set ng/m3 |  | 0.0496 | 0.0103 | 0.0879 | - | -
Anthanthrene | 6-8hrs | None set µg/m3 |  | 0.12 | 0.04 | <0.0056 | - | -
Benzo(a)anthracene | 6-8hrs | None set µg/m3 |  | <0.0056 | <0.0059 | <0.0056 | - | -
Benzo(a)pyrene | 6-8hrs | None set µg/m3 |  | <0.0056 | <0.0059 | <0.0056 | - | -
Benzo(b)fluoranthene | 6-8hrs | None set µg/m3 |  | <0.0056 | <0.0059 | <0.0056 | - | -
Benzo(b)naptho(2,1-d) thiophene | 6-8hrs | None set µg/m3 |  | <0.0075 | <0.0079 | <0.0075 | - | -
Benzo(c)phenanthrene | 6-8hrs | None set µg/m3 |  | <0.0075 | <0.0079 | <0.0075 | - | -
Benzo(ghi)perylene | 6-8hrs | None set µg/m3 |  | <0.0056 | <0.0059 | <0.0056 | - | -
Benzo(k)fluoranthene | 6-8hrs | None set µg/m3 |  | <0.0056 | <0.0059 | <0.0056 | - | -
Cholanthrene | 6-8hrs | None set µg/m3 |  | <0.0075 | <0.0079 | <0.0075 | - | -
Chrysene | 6-8hrs | None set µg/m3 |  | <0.0056 | <0.0059 | <0.0056 | - | -
Cyclopenta(cd)pyrene | 6-8hrs | None set µg/m3 |  | <0.0075 | <0.0079 | <0.0075 | - | -
Dibenzo(ai)pyrene | 6-8hrs | None set µg/m3 |  | <0.0056 | <0.0099 | <0.0094 | - | -
Dibenzo(ah)anthracene | 6-8hrs | None set µg/m3 |  | 0.02 | 0.01 | <0.0056 | - | -
Fluoranthene | 6-8hrs | None set µg/m3 |  | 0.01 | 0.01 | <0.0056 | - | -
Indeno(123-cd) pyrene | 6-8hrs | None set µg/m3 |  | 0.01 | <0.0059 | <0.0056 | - | -
Naphthalene | 6-8hrs | None set µg/m3 |  | 0.17 | 0.14 | 0.38 | - | -
Comments :
Signed |  |  |  |  | Date | 2021-03-08

## Air Q2 (periodic)
Annual Performance Report 2020 |  |  | Full Circle Generation Ltd
Emissions to Air (periodically monitored)
Summary of monitoring undertaken, standards used and compliance | [8 empty] | Notes:
A1 Testing Duration : 21 to 22 April 2020 A2 Testing Duration : 8 to 9 April 2020 A3 Testing Duration : 6 to 7 April 2020 | [8 empty] | Template may require adjustment for any bespoke monitoring requirements of permit.
Results of emissions to air that are periodically monitored
Substance | Ref. Period | Emission Limit Value |  | Average |  |  |  |  | User to add additional tables as necessary, depending on whether quarterly or bi-annual reporting is required for the compliance year
|  |  |  | A1 | A2 | A3 | A4 | A5
Hydrogen fluoride | 1 hr | 2 mg/m3 |  | 0.12 | 0.19 | 1.65 | - | -
Cd and Tl and their compounds | 6-8hrs | 0.05 mg/m3 |  | 0.0028 | 0.0031 | 0.0043 | - | -
Hg and its compounds | 6-8hrs | 0.05 mg/m3 |  | 0.0013 | 0.0007 | 0.0163 | - | -
Sb, As, Pb, Cr, Co, Cu, Mn, Ni, V and their compounds | 6-8hrs | 0.5 mg/m3 |  | - | - | - | - | -
Dioxins & Furans (I-TEQ) | 6-8hrs | 0.1 ng/m3 |  | 0.1772 | 0.0518 | 0.0325 | - | -
PCBs (WHO-TEQ Humans / Mammals) | 6-8hrs | None set ng/m3 |  | 0.0118 | 0.0047 | 0.0028 | - | -
PCBs (WHO-TEQ Fish) | 6-8hrs | None set ng/m3 |  | 0.0005 | 0.0002 | 0.0001 | - | -
PCBs (WHO-TEQ Birds) | 6-8hrs | None set ng/m3 |  | 0.0164 | 0.0082 | 0.0051 | - | -
Dioxins & Furans (WHO-TEQ Humans / Mammals) | 6-8hrs | None set ng/m3 |  | 0.1639 | 0.0473 | 0.0297 | - | -
Dioxins & Furans (WHO-TEQ Fish) | 6-8hrs | None set ng/m3 |  | 0.1476 | 0.0479 | 0.0294 | - | -
Dioxins & Furans (WHO-TEQ Birds) | 6-8hrs | None set ng/m3 |  | 0.1874 | 0.0679 | 0.0389 | - | -
Anthanthrene | 6-8hrs | None set µg/m3 |  | <0.0138 | <0.0166 | <0.013 | - | -
Benzo(a)anthracene | 6-8hrs | None set µg/m3 |  | <0.0138 | <0.0166 | <0.013 | - | -
Benzo(a)pyrene | 6-8hrs | None set µg/m3 |  | <0.0138 | <0.0166 | <0.013 | - | -
Benzo(b)fluoranthene | 6-8hrs | None set µg/m3 |  | <0.0138 | <0.0166 | <0.013 | - | -
Benzo(b)naptho(2,1-d) thiophene | 6-8hrs | None set µg/m3 |  | <0.0183 | <0.0221 | <0.0174 | - | -
Benzo(c)phenanthrene | 6-8hrs | None set µg/m3 |  | <0.0183 | <0.0221 | <0.0174 | - | -
Benzo(ghi)perylene | 6-8hrs | None set µg/m3 |  | <0.0138 | <0.0166 | <0.013 | - | -
Benzo(k)fluoranthene | 6-8hrs | None set µg/m3 |  | <0.0138 | <0.0166 | <0.013 | - | -
Cholanthrene | 6-8hrs | None set µg/m3 |  | <0.0183 | <0.0221 | <0.0174 | - | -
Chrysene | 6-8hrs | None set µg/m3 |  | <0.0183 | <0.0166 | <0.013 | - | -
Cyclopenta(cd)pyrene | 6-8hrs | None set µg/m3 |  | <0.0138 | <0.0221 | <0.0174 | - | -
Dibenzo(ai)pyrene | 6-8hrs | None set µg/m3 |  | <0.0229 | <0.0277 | <0.0217 | - | -
Dibenzo(ah)anthracene | 6-8hrs | None set µg/m3 |  | <0.0138 | 0.02 | 0.02 | - | -
Fluoranthene | 6-8hrs | None set µg/m3 |  | <0.0138 | 0.04 | 0.03 | - | -
Indeno(123-cd) pyrene | 6-8hrs | None set µg/m3 |  | <0.0138 | <0.0166 | <0.013 | - | -
Naphthalene | 6-8hrs | None set µg/m3 |  | 0.23 | 0.22 | 0.17 | - | -
Comments :
Signed |  |  |  |  | Date | 2021-03-08

## Air Q3 (periodic)
Annual Performance Report 2020 |  |  | Full Circle Generation Ltd
Emissions to Air (periodically monitored)
Summary of monitoring undertaken, standards used and compliance | [8 empty] | Notes:
A1 Testing Duration : 31 to 10 Sept 2020 A2 Testing Duration : 31 to 10 Sept 2020 A3 Testing Duration : 31 to 10 Sept 2020 | [8 empty] | Template may require adjustment for any bespoke monitoring requirements of permit.
Results of emissions to air that are periodically monitored
Substance | Ref. Period | Emission Limit Value |  | Average |  |  |  |  | User to add additional tables as necessary, depending on whether quarterly or bi-annual reporting is required for the compliance year
|  |  |  | A1 | A2 | A3 | A4 | A5
Hydrogen fluoride | 1 hr | 2 mg/m3 |  | 0.12 | 0.02 | 0.01 | - | -
Cd and Tl and their compounds | 6-8hrs | 0.05 mg/m3 |  | 0.0015 | 0.0021 | 0.0026 | - | -
Hg and its compounds | 6-8hrs | 0.05 mg/m3 |  | 0.0034 | 0.001 | 0.0016 | - | -
Sb, As, Pb, Cr, Co, Cu, Mn, Ni, V and their compounds | 6-8hrs | 0.5 mg/m3 |  | - | - | - | - | -
Dioxins & Furans (I-TEQ) | 6-8hrs | 0.1 ng/m3 |  | 0.0161 | 0.0046 | 0.0204 | - | -
PCBs (WHO-TEQ Humans / Mammals) | 6-8hrs | None set ng/m3 |  | 0.0013 | 0.0006 | 0.0014 | - | -
PCBs (WHO-TEQ Fish) | 6-8hrs | None set ng/m3 |  | 0.0001 | 0 | 0.003 | - | -
PCBs (WHO-TEQ Birds) | 6-8hrs | None set ng/m3 |  | 0.002 | 0.0013 | 0.0022 | - | -
Dioxins & Furans (WHO-TEQ Humans / Mammals) | 6-8hrs | None set ng/m3 |  | 0.0151 | 0.0042 | 0.0208 | - | -
Dioxins & Furans (WHO-TEQ Fish) | 6-8hrs | None set ng/m3 |  | 0.014 | 0.0044 | 0.0206 | - | -
Dioxins & Furans (WHO-TEQ Birds) | 6-8hrs | None set ng/m3 |  | 0.0175 | 0.0059 | 0.0298 | - | -
Anthanthrene | 6-8hrs | None set µg/m3 |  | <0.0056 | <0.0056 | <0.0026 | - | -
Benzo(a)anthracene | 6-8hrs | None set µg/m3 |  | <0.0056 | 0.01 | <0.0026 | - | -
Benzo(a)pyrene | 6-8hrs | None set µg/m3 |  | <0.0056 | 0.01 | <0.0026 | - | -
Benzo(b)fluoranthene | 6-8hrs | None set µg/m3 |  | <0.0056 | 0.01 | <0.0026 | - | -
Benzo(b)naptho(2,1-d) thiophene | 6-8hrs | None set µg/m3 |  | <0.0056 | <0.0056 | <0.0026 | - | -
Benzo(c)phenanthrene | 6-8hrs | None set µg/m3 |  | <0.0056 | <0.0056 | <0.0026 | - | -
Benzo(ghi)perylene | 6-8hrs | None set µg/m3 |  | <0.0056 | <0.0056 | <0.0026 | - | -
Benzo(k)fluoranthene | 6-8hrs | None set µg/m3 |  | <0.0056 | <0.0056 | <0.0026 | - | -
Cholanthrene | 6-8hrs | None set µg/m3 |  | <0.0056 | <0.0056 | <0.0026 | - | -
Chrysene | 6-8hrs | None set µg/m3 |  | <0.0056 | <0.0056 | 0 | - | -
Cyclopenta(cd)pyrene | 6-8hrs | None set µg/m3 |  | <0.0056 | <0.0056 | <0.0026 | - | -
Dibenzo(ai)pyrene | 6-8hrs | None set µg/m3 |  | <0.0056 | <0.0056 | <0.0026 | - | -
Dibenzo(ah)anthracene | 6-8hrs | None set µg/m3 |  | <0.0056 | <0.0056 | <0.0026 | - | -
Fluoranthene | 6-8hrs | None set µg/m3 |  | 0.02 | 0.03 | 0.03 | - | -
Indeno(123-cd) pyrene | 6-8hrs | None set µg/m3 |  | <0.0056 | <0.0056 | <0.0026 | - | -
Naphthalene | 6-8hrs | None set µg/m3 |  | 2.86 | 3.84 | 3.57 | - | -
Comments :
Signed |  |  |  |  | Date | 2021-03-08

## Air Q4 (periodic)
Annual Performance Report 2020 |  |  | Full Circle Generation Ltd
Emissions to Air (periodically monitored)
Summary of monitoring undertaken, standards used and compliance | [8 empty] | Notes:
Test Postponed to 2021 Due to planned Major Outage Work in late Q4. | [8 empty] | Template may require adjustment for any bespoke monitoring requirements of permit.
Results of emissions to air that are periodically monitored
Substance | Ref. Period | Emission Limit Value |  | Average |  |  |  |  | User to add additional tables as necessary, depending on whether quarterly or bi-annual reporting is required for the compliance year
|  |  |  | A1 | A2 | A3 | A4 | A5
Hydrogen fluoride | 1 hr | 2 mg/m3 |  | - | - | - | - | -
Cd and Tl and their compounds | 6-8hrs | 0.05 mg/m3 |  | - | - | - | - | -
Hg and its compounds | 6-8hrs | 0.05 mg/m3 |  | - | - | - | - | -
Sb, As, Pb, Cr, Co, Cu, Mn, Ni, V and their compounds | 6-8hrs | 0.5 mg/m3 |  | - | - | - | - | -
Dioxins & Furans (I-TEQ) | 6-8hrs | 0.1 ng/m3 |  | - | - | - | - | -
PCBs (WHO-TEQ Humans / Mammals) | 6-8hrs | None set ng/m3 |  | - | - | - | - | -
PCBs (WHO-TEQ Fish) | 6-8hrs | None set ng/m3 |  | - | - | - | - | -
PCBs (WHO-TEQ Birds) | 6-8hrs | None set ng/m3 |  | - | - | - | - | -
Dioxins & Furans (WHO-TEQ Humans / Mammals) | 6-8hrs | None set ng/m3 |  | - | - | - | - | -
Dioxins & Furans (WHO-TEQ Fish) | 6-8hrs | None set ng/m3 |  | - | - | - | - | -
Dioxins & Furans (WHO-TEQ Birds) | 6-8hrs | None set ng/m3 |  | - | - | - | - | -
Anthanthrene | 6-8hrs | None set µg/m3 |  | - | - | - | - | -
Benzo(a)anthracene | 6-8hrs | None set µg/m3 |  | - | - | - | - | -
Benzo(a)pyrene | 6-8hrs | None set µg/m3 |  | - | - | - | - | -
Benzo(b)fluoranthene | 6-8hrs | None set µg/m3 |  | - | - | - | - | -
Benzo(b)naptho(2,1-d) thiophene | 6-8hrs | None set µg/m3 |  | - | - | - | - | -
Benzo(c)phenanthrene | 6-8hrs | None set µg/m3 |  | - | - | - | - | -
Benzo(ghi)perylene | 6-8hrs | None set µg/m3 |  | - | - | - | - | -
Benzo(k)fluoranthene | 6-8hrs | None set µg/m3 |  | - | - | - | - | -
Cholanthrene | 6-8hrs | None set µg/m3 |  | - | - | - | - | -
Chrysene | 6-8hrs | None set µg/m3 |  | - | - | - | - | -
Cyclopenta(cd)pyrene | 6-8hrs | None set µg/m3 |  | - | - | - | - | -
Dibenzo(ai)pyrene | 6-8hrs | None set µg/m3 |  | - | - | - | - | -
Dibenzo(ah)anthracene | 6-8hrs | None set µg/m3 |  | - | - | - | - | -
Fluoranthene | 6-8hrs | None set µg/m3 |  | - | - | - | - | -
Indeno(123-cd) pyrene | 6-8hrs | None set µg/m3 |  | - | - | - | - | -
Naphthalene | 6-8hrs | None set µg/m3 |  | - | - | - | - | -
Comments :
Signed |  |  |  |  | Date | 2021-03-08

## Air (CEMS)
Annual Performance Report 2020 | [7 empty] | Full Circle Generation Ltd
Emissions to Air (continously monitored)
Notes:
Summary of monitoring undertaken, standards used and compliance | [12 empty] | Template may require adjustment for any bespoke monitoring requirements of permit
Report to 2 decimal places, i.e. xx.xx%
Results of emissions to air that are continuously monitored (maximum and average values for each line)
Substance | Reference Period | Emission Limit Value | A1 |  | A2 |  | A3 |  | A4 |  | A5
|  |  | Max. | Avg. | Max. | Avg. | Max. | Avg. | Max. | Avg. | Max. | Avg.
Oxides of nitrogen | Daily mean | 170 mg/m3 | 137.1 | 47.4833 | 119.7 | 65.7667 | 136 | 55.075
| *(100%) ½ hourly mean | 400 mg/m3 | N/A | N/A | N/A | N/A | N/A | N/A
| *(97%) ½ hourly mean | 200 mg/m3 | 204 | 46.825 | 426.5 | 65.3167 | 183.2 | 54.825
Particulates | Daily mean | 10 mg/m3 | 1.5 | 0.24167 | 1.8 | 0.23333 | 0.1 | 0
| *(100%) ½ hourly mean | 30 mg/m3 | N/A | N/A | N/A | N/A | N/A | N/A
| *(97%) ½ hourly mean | 10mg/m3 | 29.1 | 0.28333 | 9.2 | 0.275 | 0.5 | 0
Total Organic Carbon | Daily mean | 10 mg/m3 | 5.2 | 0.13333 | 2.5 | 0.066667 | 2.7 | 0.10833
| *(100%)½ hourly mean | 20 mg/m3 | N/A | N/A | N/A | N/A | N/A | N/A
| *(97%) ½ hourly mean | 10 mg/m3 | 1224.4 | 0.28333 | 75.7 | 0.075 | 166.7 | 0.14167
Hydrogen chloride | Daily mean | 10 mg/m3 | 9.4 | 6.7417 | 15.3 | 6.775 | 13.4 | 6.8
| (100%)½ hourly mean | 60 mg/m3 | N/A | N/A | N/A | N/A | N/A | N/A
| *(97%) ½ hourly mean | 10 mg/m3 | 74.1 | 6.8417 | 281.2 | 6.875 | 143.5 | 6.8917
Sulphur dioxide | Daily mean | 50 mg/m3 | 70.9 | 3.7583 | 13.1 | 4.0667 | 13.8 | 3.0333
| (100%)½ hourly mean | 200 mg/m3 | N/A | N/A | N/A | N/A | N/A | N/A
| (97%)½ hourly mean | 50 mg/m3 | 880.8 | 3.7833 | 250.9 | 4.1392 | 497.6 | 3.1167
Carbon monoxide | Daily mean | 50 mg/m3 | 86.2 | 1.2167 | 26.8 | 0.625 | 22.2 | 0.78333
| ½ hourly mean * | 100 mg/m3 * | N/A | N/A | N/A | N/A | N/A | N/A
| 95%ile 10-min avg * | 150 mg/m3 * | 65.2583 | 1.075 | 13.4917 | 0.63333 | 51.2833 | 0.75833
Ammonia | Daily mean | No limit set | 21.9 | 0.28333 | 3.9 | 0.075 | 3 | 0.14167
* = delete or amend as appropriate
Comments :
Signed | [7 empty] | Date | 2021-03-08

## HCl
Annual Performance Report 2020 |  |  |  | Full Circle Generation Ltd
Monitoring of Hydrogen Chloride emissions |  |  | Whole Installation |  |  | See Notes in Cell Q3 | Monitoring of Hydrogen Chloride emissions |  |  |  | Per Combustion Line |  | Notes:
User to add logic to complete Whole installation, Table A5:G18. From the data in Per Combustion Line, Table J6:O79, subject to No. of lines installed
mg/Nm3 | 1/2 Hourly Reference Periods |  |  | Daily Reference Periods
2020 | (97%) 1/2 hourly HCl ELV | Monthly 1/2 hourly mean | Highest 1/2 hourly maximum | Daily HCl ELV | Monthly daily mean | Highest daily maximum | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
Jan | 10 | 8.1667 | 55.8 | 10 | 8 | 9.4333 | A1 | Jan | 8.1 | 26 | 7.8 | 9
Feb | 10 | 8.1667 | 39.6333 | 10 | 8.0667 | 9.2333 |  | Feb | 8.1 | 33.8 | 8 | 8.9
Mar | 10 | 8.2667 | 166.1667 | 10 | 8.2333 | 12.6333 |  | Mar | 8.3 | 73.8 | 8.2 | 9.2 | Whole Installation table A5:G18:
Apr | 10 | 8.3 | 42.0333 | 10 | 8.2333 | 9.2333 |  | Apr | 8.4 | 53.4 | 8.4 | 9.4 | Mean: for 1/2 hourly and daily periods calculate mean of values across all operational combustion lines for the month
May | 10 | 8.2333 | 32.9667 | 10 | 8.2333 | 8.7 |  | May | 8.3 | 40.2 | 8.3 | 8.8
Jun | 10 | 8.3667 | 41.3 | 10 | 8.2667 | 9.1667 |  | Jun | 8.4 | 67.7 | 8.3 | 9.4
Jul | 10 | 8.1667 | 43.7333 | 10 | 7.7667 | 9.1 |  | Jul | 8.2 | 74.1 | 7.6 | 9 | Maximum: for 1/2 hourly and daily periods use the highest value across all operational combustion lines for the month
Aug | 10 | 8.4333 | 15.1 | 10 | 8.2333 | 8.6333 |  | Aug | 8.5 | 16.7 | 8.4 | 8.7
Sep | 10 | 8.2 | 28.8 | 10 | 8.1333 | 8.8333 |  | Sep | 8.3 | 29.3 | 8.4 | 8.9
Oct | 10 | 8.1333 | 65.1667 | 10 | 8.1 | 9.3 |  | Oct | 7.5 | 59.9 | 7.5 | 8.9
Nov | 10 | 0 | 0 | 10 | 0 | 0 |  | Nov | 0 | 0 | 0 | 0
Dec | 10 | 0 | 0 | 10 | 0 | 0 |  | Dec | 0 | 0 | 0 | 0
[8 empty] | Annual | 6.8417 | 74.1 | 6.7417 | 9.4
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A2 | Jan | 8.2 | 103.1 | 8.1 | 10.3
[8 empty] | Feb | 8.1 | 52.7 | 7.9 | 9
[8 empty] | Mar | 8.1 | 281.2 | 8.1 | 15.3
[8 empty] | Apr | 8.1 | 19.4 | 8 | 8.4
[8 empty] | May | 8.1 | 29.6 | 8.1 | 8.5
[8 empty] | Jun | 8.3 | 14.3 | 8.2 | 8.6
[8 empty] | Jul | 8.5 | 43.4 | 8.5 | 9.8
[8 empty] | Aug | 8.5 | 10.8 | 8.1 | 8.6
[8 empty] | Sep | 8.1 | 20.5 | 7.9 | 8.6
[8 empty] | Oct | 8.5 | 46 | 8.4 | 9.3
[8 empty] | Nov | 0 | 0 | 0 | 0
[8 empty] | Dec | 0 | 0 | 0 | 0
[8 empty] | Annual | 6.875 | 281.2 | 6.775 | 15.3
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A3 | Jan | 8.2 | 38.3 | 8.1 | 9
[8 empty] | Feb | 8.3 | 32.4 | 8.3 | 9.8
[8 empty] | Mar | 8.4 | 143.5 | 8.4 | 13.4
[8 empty] | Apr | 8.4 | 53.3 | 8.3 | 9.9
[8 empty] | May | 8.3 | 29.1 | 8.3 | 8.8
[8 empty] | Jun | 8.4 | 41.9 | 8.3 | 9.5
[8 empty] | Jul | 7.8 | 13.7 | 7.2 | 8.5
[8 empty] | Aug | 8.3 | 17.8 | 8.2 | 8.6
[8 empty] | Sep | 8.2 | 36.6 | 8.1 | 9
[8 empty] | Oct | 8.4 | 89.6 | 8.4 | 9.7
[8 empty] | Nov | 0 | 0 | 0 | 0
Comments : | [7 empty] | Dec | 0 | 0 | 0 | 0
[8 empty] | Annual | 6.8917 | 143.5 | 6.8 | 13.4
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A4 | Jan
Feb
Mar
Apr
May
Jun
Signed |  |  |  | Date | 2021-03-08 |  |  | Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A5 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0

## SO2
Annual Performance Report 2020 |  |  |  | Full Circle Generation Ltd
Monitoring of Sulphur dioxide emissions |  |  | Whole Installation |  |  | See Notes in Cell Q3 | Monitoring of Sulphur dioxide emissions |  |  |  | Per Combustion Line |  | Notes:
User to add logic to complete Whole installation, Table A5:G18. From the data in Per Combustion Line, Table J6:O79, subject to No. of lines installed
mg/Nm3 | 1/2 Hourly Reference Periods |  |  | Daily Reference Periods
2020 | (97%) 1/2 hourly SO2 ELV | Monthly 1/2 hourly mean | Highest 1/2 hourly maximum | Daily SO2 ELV | Monthly daily mean | Highest daily maximum | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
Jan | 50 | 2.4233 | 172.5 | 50 | 2.1333 | 8 | A1 | Jan | 1.8 | 15.4 | 1.7 | 2.6
Feb | 50 | 2.4333 | 134.9333 | 50 | 2.3667 | 5.0333 |  | Feb | 2.5 | 153.7 | 2.4 | 5.6
Mar | 50 | 5.2333 | 411.8667 | 50 | 5.4 | 30.6333 |  | Mar | 7.6 | 880.8 | 8 | 70.9 | Whole Installation table A5:G18:
Apr | 50 | 4.7667 | 241.4 | 50 | 4.7333 | 10.1333 |  | Apr | 4.5 | 119.7 | 4.5 | 6.8 | Mean: for 1/2 hourly and daily periods calculate mean of values across all operational combustion lines for the month
May | 50 | 4.3 | 154.0667 | 50 | 4.3 | 8.6667 |  | May | 4.2 | 283 | 4.2 | 10.7
Jun | 50 | 4.4333 | 187.6667 | 50 | 4.4333 | 10.7333 |  | Jun | 4.5 | 526.8 | 4.6 | 21.5
Jul | 50 | 5.8333 | 137.9333 | 50 | 5.6667 | 9.8667 |  | Jul | 5.9 | 214.9 | 5.6 | 10.6 | Maximum: for 1/2 hourly and daily periods use the highest value across all operational combustion lines for the month
Aug | 50 | 6.9333 | 12.0667 | 50 | 6.7 | 8.1667 |  | Aug | 7.2 | 11.6 | 7 | 8
Sep | 50 | 4.0667 | 60.0667 | 50 | 4 | 5.9667 |  | Sep | 3.6 | 157.5 | 3.5 | 6.6
Oct | 50 | 3.7333 | 145.7333 | 50 | 3.7 | 7.1 |  | Oct | 3.6 | 413.7 | 3.6 | 12.4
Nov | 50 | 0 | 0 | 50 | 0 | 0 |  | Nov | 0 | 0 | 0 | 0
Dec | 50 | 0 | 0 | 50 | 0 | 0 |  | Dec | 0 | 0 | 0 | 0
[8 empty] | Annual | 3.7833 | 880.8 | 3.7583 | 70.9
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A2 | Jan | 2.87 | 250.9 | 2.6 | 13
[8 empty] | Feb | 2.4 | 131.8 | 2.3 | 4.9
[8 empty] | Mar | 4.2 | 118.5 | 4.3 | 9.3
[8 empty] | Apr | 5.8 | 106.9 | 5.8 | 9.8
[8 empty] | May | 5 | 61.3 | 5 | 6.6
[8 empty] | Jun | 5.1 | 21.9 | 5 | 5.5
[8 empty] | Jul | 8.1 | 189.9 | 8 | 13.1
[8 empty] | Aug | 7.2 | 9.7 | 6.8 | 7.2
[8 empty] | Sep | 4.6 | 8.8 | 4.6 | 5.9
[8 empty] | Oct | 4.4 | 8.1 | 4.4 | 5.1
[8 empty] | Nov | 0 | 0 | 0 | 0
[8 empty] | Dec | 0 | 0 | 0 | 0
[8 empty] | Annual | 4.1392 | 250.9 | 4.0667 | 13.1
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A3 | Jan | 2.6 | 251.2 | 2.1 | 8.4
[8 empty] | Feb | 2.4 | 119.3 | 2.4 | 4.6
[8 empty] | Mar | 3.9 | 236.3 | 3.9 | 11.7
[8 empty] | Apr | 4 | 497.6 | 3.9 | 13.8
[8 empty] | May | 3.7 | 117.9 | 3.7 | 8.7
[8 empty] | Jun | 3.7 | 14.3 | 3.7 | 5.2
[8 empty] | Jul | 3.5 | 9 | 3.4 | 5.9
[8 empty] | Aug | 6.4 | 14.9 | 6.3 | 9.3
[8 empty] | Sep | 4 | 13.9 | 3.9 | 5.4
[8 empty] | Oct | 3.2 | 15.4 | 3.1 | 3.8
[8 empty] | Nov | 0 | 0 | 0 | 0
Comments : | [7 empty] | Dec | 0 | 0 | 0 | 0
[8 empty] | Annual | 3.1167 | 497.6 | 3.0333 | 13.8
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A4 | Jan
Feb
Mar
Apr
May
Signed |  |  |  | Date | 2021-03-08 |  |  | Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A5 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0

## NOx
Annual Performance Report 2020 |  |  |  | Full Circle Generation Ltd
Monitoring of Oxides of Nitrogen emissions |  |  | Whole Installation |  |  | See Notes in Cell Q3 | Monitoring of Oxides of Nitrogen emissions |  |  |  | Per Combustion Line |  | Notes:
User to add logic to complete Whole installation, Table A5:G18. From the data in Per Combustion Line, Table J6:O79, subject to No. of lines installed
mg/Nm3 | 1/2 Hourly Reference Periods |  |  | Daily Reference Periods
2020 | (97%)1/2 hourly NOx ELV | Monthly 1/2 hourly mean | Highest 1/2 hourly maximum | Daily NOx ELV | Monthly daily mean | Highest daily maximum | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
Jan | 200 | 87.7 | 195.5667 | 170 | 88.6 | 123.8333 | A1 | Jan | 91.5 | 204 | 94 | 137.1
Feb | 200 | 65.7333 | 264.4333 | 170 | 66.4 | 111.6667 |  | Feb | 61 | 192.7 | 62.5 | 91.3
Mar | 200 | 68.7667 | 210.7333 | 170 | 69.5667 | 115.7667 |  | Mar | 68 | 189.3 | 69 | 106 | Whole Installation table A5:G18:
Apr | 200 | 47.8 | 164.9333 | 170 | 48.0667 | 75.5667 |  | Apr | 34.9 | 157.1 | 34.9 | 50.5 | Mean: for 1/2 hourly and daily periods calculate mean of values across all operational combustion lines for the month
May | 200 | 55.7333 | 147.0667 | 170 | 56.3333 | 96.5667 |  | May | 42.4 | 150 | 42.9 | 60.4
Jun | 200 | 57.1 | 156.9667 | 170 | 57.5667 | 104.6667 |  | Jun | 42.6 | 185.4 | 43 | 106.1
Jul | 200 | 72.9 | 146.0667 | 170 | 73.8667 | 99.5 |  | Jul | 58.3 | 154.3 | 60.6 | 85.5 | Maximum: for 1/2 hourly and daily periods use the highest value across all operational combustion lines for the month
Aug | 200 | 81 | 133.1333 | 170 | 81.0667 | 93.2 |  | Aug | 58.8 | 124.4 | 58.7 | 64.3
Sep | 200 | 62.1667 | 151.4667 | 170 | 62.8 | 97.3333 |  | Sep | 50.1 | 132.5 | 49.9 | 81.4
Oct | 200 | 68.9667 | 123.2 | 170 | 69.0333 | 91.2333 |  | Oct | 54.3 | 112.7 | 54.3 | 78.2
Nov | 200 | 0 | 0 | 170 | 0 | 0 |  | Nov | 0 | 0 | 0 | 0
Dec | 200 | 0 | 0 | 170 | 0 | 0 |  | Dec | 0 | 0 | 0 | 0
[8 empty] | Annual | 46.825 | 204 | 47.4833 | 137.1
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A2 | Jan | 87.8 | 199.5 | 87.5 | 116
[8 empty] | Feb | 66.3 | 426.5 | 68 | 107.7
[8 empty] | Mar | 83.2 | 282.1 | 83.5 | 117.5
[8 empty] | Apr | 68.8 | 164.6 | 68.7 | 90.1
[8 empty] | May | 79.5 | 145.2 | 79.5 | 119.7
[8 empty] | Jun | 69.1 | 131.7 | 70.1 | 112.8
[8 empty] | Jul | 85.9 | 131.7 | 86 | 112
[8 empty] | Aug | 99.7 | 127.3 | 99.9 | 104.1
[8 empty] | Sep | 51.8 | 164.3 | 54 | 99.8
[8 empty] | Oct | 91.7 | 126.2 | 92 | 107.3
[8 empty] | Nov | 0 | 0 | 0 | 0
[8 empty] | Dec | 0 | 0 | 0 | 0
[8 empty] | Annual | 65.3167 | 426.5 | 65.7667 | 119.7
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A3 | Jan | 83.8 | 183.2 | 84.3 | 118.4
[8 empty] | Feb | 69.9 | 174.1 | 68.7 | 136
[8 empty] | Mar | 55.1 | 160.8 | 56.2 | 123.8
[8 empty] | Apr | 39.7 | 173.1 | 40.6 | 86.1
[8 empty] | May | 45.3 | 146 | 46.6 | 109.6
[8 empty] | Jun | 59.6 | 153.8 | 59.6 | 95.1
[8 empty] | Jul | 74.5 | 152.2 | 75 | 101
[8 empty] | Aug | 84.5 | 147.7 | 84.6 | 111.2
[8 empty] | Sep | 84.6 | 157.6 | 84.5 | 110.8
[8 empty] | Oct | 60.9 | 130.7 | 60.8 | 88.2
[8 empty] | Nov | 0 | 0 | 0 | 0
Comments : | [7 empty] | Dec | 0 | 0 | 0 | 0
[8 empty] | Annual | 54.825 | 183.2 | 55.075 | 136
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A4 | Jan
Feb
Mar
Apr
May
Jun
Signed |  |  |  | Date | 2021-03-08 |  |  | Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A5 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0

## TOC
Annual Performance Report 2020 |  |  |  | Full Circle Generation Ltd
Monitoring of Total organic carbon emissions |  |  | Whole Installation |  |  | See Notes in Cell Q3 | Monitoring of Total organic carbon emissions |  |  |  | Per Combustion Line |  | Notes:
User to add logic to complete Whole installation, Table A5:G18. From the data in Per Combustion Line, Table J6:O79, subject to No. of lines installed
mg/Nm3 | 1/2 Hourly Reference Periods |  |  | Daily Reference Periods
2020 | (97%) 1/2 hourly TOC ELV | Monthly 1/2 hourly mean | Highest 1/2 hourly maximum | Daily TOC ELV | Monthly daily mean | Highest daily maximum | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
Jan | 10 | 0.46667 | 73.6 | 10 | 0.3 | 1.1333 | A1 | Jan | 0.4 | 0.9 | 0.3 | 0.6
Feb | 10 | 0.33333 | 7.6 | 10 | 0.3 | 0.53333 |  | Feb | 0.3 | 2.2 | 0.3 | 0.4
Mar | 10 | 1.0333 | 450.9333 | 10 | 0.46667 | 3.4333 |  | Mar | 2.5 | 1224.4 | 0.8 | 5.2 | Whole Installation table A5:G18:
Apr | 10 | 0.033333 | 3.1667 | 10 | 0.033333 | 0.9 |  | Apr | 0 | 0.9 | 0 | 0 | Mean: for 1/2 hourly and daily periods calculate mean of values across all operational combustion lines for the month
May | 10 | 0.066667 | 37.5667 | 10 | 0.066667 | 1.2667 |  | May | 0.1 | 106.4 | 0.1 | 2.5
Jun | 10 | 0.033333 | 23.8 | 10 | 0.033333 | 0.96667 |  | Jun | 0.1 | 70.3 | 0.1 | 2.8
Jul | 10 | 0.033333 | 2.6333 | 10 | 0.033333 | 0.1 |  | Jul | 0 | 1.3 | 0 | 0 | Maximum: for 1/2 hourly and daily periods use the highest value across all operational combustion lines for the month
Aug | 10 | 0 | 0.16667 | 10 | 0 | 0 |  | Aug | 0 | 0.1 | 0 | 0
Sep | 10 | 0 | 1.1667 | 10 | 0 | 0.066667 |  | Sep | 0 | 1.7 | 0 | 0.1
Oct | 10 | 0 | 1.6333 | 10 | 0 | 0.1 |  | Oct | 0 | 3.1 | 0 | 0.2
Nov | 10 | 0 | 0 | 10 | 0 | 0 |  | Nov | 0 | 0 | 0 | 0
Dec | 10 | 0 | 0 | 10 | 0 | 0 |  | Dec | 0 | 0 | 0 | 0
[8 empty] | Annual | 0.28333 | 1224.4 | 0.13333 | 5.2
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A2 | Jan | 0.4 | 53.2 | 0.3 | 2.1
[8 empty] | Feb | 0.3 | 16 | 0.3 | 0.6
[8 empty] | Mar | 0.2 | 75.7 | 0.2 | 2.5
[8 empty] | Apr | 0 | 1.6 | 0 | 0
[8 empty] | May | 0 | 3.7 | 0 | 0.3
[8 empty] | Jun | 0 | 0.6 | 0 | 0
[8 empty] | Jul | 0 | 1.4 | 0 | 0
[8 empty] | Aug | 0 | 0.1 | 0 | 0
[8 empty] | Sep | 0 | 0.4 | 0 | 0
[8 empty] | Oct | 0 | 0.6 | 0 | 0
[8 empty] | Nov | 0 | 0 | 0 | 0
[8 empty] | Dec | 0 | 0 | 0 | 0
[8 empty] | Annual | 0.075 | 75.7 | 0.066667 | 2.5
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A3 | Jan | 0.6 | 166.7 | 0.3 | 0.7
[8 empty] | Feb | 0.4 | 4.6 | 0.3 | 0.6
[8 empty] | Mar | 0.4 | 52.7 | 0.4 | 2.6
[8 empty] | Apr | 0.1 | 7 | 0.1 | 2.7
[8 empty] | May | 0.1 | 2.6 | 0.1 | 1
[8 empty] | Jun | 0 | 0.5 | 0 | 0.1
[8 empty] | Jul | 0.1 | 5.2 | 0.1 | 0.3
[8 empty] | Aug | 0 | 0.3 | 0 | 0
[8 empty] | Sep | 0 | 1.4 | 0 | 0.1
[8 empty] | Oct | 0 | 1.2 | 0 | 0.1
[8 empty] | Nov | 0 | 0 | 0 | 0
Comments : | [7 empty] | Dec | 0 | 0 | 0 | 0
[8 empty] | Annual | 0.14167 | 166.7 | 0.10833 | 2.7
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A4 | Jan
Feb
Mar
Apr
May
Signed |  |  |  | Date | 2021-03-08 |  |  | Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A5 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0

## Particulates
Annual Performance Report 2020 |  |  |  | Full Circle Generation Ltd
Monitoring of Particulate matter emissions |  |  | Whole Installation |  |  | See Notes in Cell Q3 | Monitoring of Particulate matter emissions |  |  |  | Per Combustion Line |  | Notes:
User to add logic to complete Whole installation, Table A5:G18. From the data in Per Combustion Line, Table J6:O79, subject to No. of lines installed
mg/Nm3 | 1/2 Hourly Reference Periods |  |  | Daily Reference Periods
2020 | (97%) 1/2 hourly PM ELV | Monthly 1/2 hourly mean | Highest 1/2 hourly maximum | Daily PM ELV | Monthly daily mean | Highest daily maximum | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
Jan | 10 | 0.033333 | 0.3 | 10 | 0 | 0.066667 | A1 | Jan | 0.1 | 0.2 | 0 | 0.1
Feb | 10 | 0.033333 | 9.8333 | 10 | 0 | 0.26667 |  | Feb | 0.1 | 29.1 | 0 | 0.7
Mar | 10 | 0.033333 | 0.33333 | 10 | 0.033333 | 0.13333 |  | Mar | 0 | 0.3 | 0 | 0.1 | Whole Installation table A5:G18:
Apr | 10 | 0.033333 | 0.23333 | 10 | 0.033333 | 0.066667 |  | Apr | 0 | 0.1 | 0 | 0 | Mean: for 1/2 hourly and daily periods calculate mean of values across all operational combustion lines for the month
May | 10 | 0.033333 | 0.23333 | 10 | 0.033333 | 0.066667 |  | May | 0 | 0.1 | 0 | 0
Jun | 10 | 0 | 0.16667 | 10 | 0 | 0.033333 |  | Jun | 0 | 0.2 | 0 | 0
Jul | 10 | 0.66667 | 3.9667 | 10 | 0.6 | 0.93333 |  | Jul | 0.5 | 2.2 | 0.4 | 0.9 | Maximum: for 1/2 hourly and daily periods use the highest value across all operational combustion lines for the month
Aug | 10 | 0.76667 | 1.2667 | 10 | 0.6 | 0.83333 |  | Aug | 0.8 | 1.4 | 0.7 | 0.9
Sep | 10 | 0.23333 | 0.8 | 10 | 0.23333 | 0.33333 |  | Sep | 0.7 | 2.1 | 0.7 | 1
Oct | 10 | 0.4 | 1.3333 | 10 | 0.36667 | 0.5 |  | Oct | 1.2 | 3.9 | 1.1 | 1.5
Nov | 10 | 0 | 0 | 10 | 0 | 0 |  | Nov | 0 | 0 | 0 | 0
Dec | 10 | 0 | 0 | 10 | 0 | 0 |  | Dec | 0 | 0 | 0 | 0
[8 empty] | Annual | 0.28333 | 29.1 | 0.24167 | 1.5
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A2 | Jan | 0 | 0.4 | 0 | 0.1
[8 empty] | Feb | 0 | 0.3 | 0 | 0.1
[8 empty] | Mar | 0.1 | 0.4 | 0.1 | 0.2
[8 empty] | Apr | 0.1 | 0.5 | 0.1 | 0.2
[8 empty] | May | 0.1 | 0.4 | 0.1 | 0.2
[8 empty] | Jun | 0 | 0.3 | 0 | 0.1
[8 empty] | Jul | 1.5 | 9.2 | 1.4 | 1.8
[8 empty] | Aug | 1.5 | 2.2 | 1.1 | 1.5
[8 empty] | Sep | 0 | 0.2 | 0 | 0
[8 empty] | Oct | 0 | 0.1 | 0 | 0
[8 empty] | Nov | 0 | 0 | 0 | 0
[8 empty] | Dec | 0 | 0 | 0 | 0
[8 empty] | Annual | 0.275 | 9.2 | 0.23333 | 1.8
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A3 | Jan | 0 | 0.3 | 0 | 0
[8 empty] | Feb | 0 | 0.1 | 0 | 0
[8 empty] | Mar | 0 | 0.3 | 0 | 0.1
[8 empty] | Apr | 0 | 0.1 | 0 | 0
[8 empty] | May | 0 | 0.2 | 0 | 0
[8 empty] | Jun | 0 | 0 | 0 | 0
[8 empty] | Jul | 0 | 0.5 | 0 | 0.1
[8 empty] | Aug | 0 | 0.2 | 0 | 0.1
[8 empty] | Sep | 0 | 0.1 | 0 | 0
[8 empty] | Oct | 0 | 0 | 0 | 0
[8 empty] | Nov | 0 | 0 | 0 | 0
Comments : | [7 empty] | Dec | 0 | 0 | 0 | 0
[8 empty] | Annual | 0 | 0.5 | 0 | 0.1
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A4 | Jan
Feb
Mar
Apr
May
Signed |  |  |  | Date | 2021-03-08 |  |  | Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A5 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0

## CO 0.5hourly
Annual Performance Report 2020 |  |  |  | Full Circle Generation Ltd
Monitoring of Carbon Monoxide (half hourly) |  |  | Whole Installation |  |  | See Notes in Cell Q3 | Monitoring of Carbon Monoxide (half hourly) |  |  |  | Per Combustion Line |  | Notes:
[7 empty] | Not applicable sheet because BYES chose 95% 10min column for CO. | [5 empty] | User to add logic to complete Whole installation, Table A5:G18. From the data in Per Combustion Line, Table J6:O79, subject to No. of lines installed
mg/Nm3 | 1/2 Hourly Reference Periods |  |  | Daily Reference Periods
2020 | 1/2 hourly CO ELV | Monthly 1/2 hourly mean | Highest 1/2 hourly maximum | Daily CO ELV | Monthly daily mean | Highest daily maximum | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
Jan | 100 |  |  | 50 |  |  | A1 | Jan
Feb | 100 |  |  | 50 |  |  |  | Feb
Mar | 100 |  |  | 50 |  |  |  | Mar |  |  |  |  | Whole Installation table A5:G18:
Apr | 100 |  |  | 50 |  |  |  | Apr |  |  |  |  | Mean: for 1/2 hourly and daily periods calculate mean of values across all operational combustion lines for the month
May | 100 |  |  | 50 |  |  |  | May
Jun | 100 |  |  | 50 |  |  |  | Jun
Jul | 100 |  |  | 50 |  |  |  | Jul |  |  |  |  | Maximum: for 1/2 hourly and daily periods use the highest value across all operational combustion lines for the month
Aug | 100 |  |  | 50 |  |  |  | Aug
Sep | 100 |  |  | 50 |  |  |  | Sep
Oct | 100 |  |  | 50 |  |  |  | Oct
Nov | 100 |  |  | 50 |  |  |  | Nov
Dec | 100 |  |  | 50 |  |  |  | Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A2 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A3 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Comments : | [7 empty] | Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A4 | Jan
Feb
Mar
Apr
May
Signed |  |  |  | Date | 2021-03-08 |  |  | Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A5 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0

## NH3
Annual Performance Report 2020 |  |  |  | Full Circle Generation Ltd
Monitoring of Ammonia emissions |  |  | Whole Installation |  |  | See Notes in Cell Q3 | Monitoring of Ammonia emissions |  |  |  | Per Combustion Line |  | Notes:
User to add logic to complete Whole installation, Table A5:G18. From the data in Per Combustion Line, Table J6:O79, subject to No. of lines installed
mg/Nm3 | 1/2 Hourly Reference Periods |  |  | Daily Reference Periods
2020 | 1/2 hourly NH3 ELV | Monthly 1/2 hourly mean | Highest 1/2 hourly maximum | Daily NH3 ELV | Monthly daily mean | Highest daily maximum | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
Jan | / | 0.3 | 48.7333 | / | 0.23333 | 1.7667 | A1 | Jan | 0.1 | 0.8 | 0 | 0.1
Feb | / | 0.16667 | 12 | / | 0.13333 | 0.73333 |  | Feb | 0.2 | 12.8 | 0.1 | 1
Mar | / | 1.0333 | 242.4667 | / | 0.76667 | 8.5 |  | Mar | 2.7 | 636.6 | 1.9 | 21.9 | Whole Installation table A5:G18:
Apr | / | 0.16667 | 5.0667 | / | 0.1 | 0.83333 |  | Apr | 0.2 | 6.7 | 0.1 | 0.4 | Mean: for 1/2 hourly and daily periods calculate mean of values across all operational combustion lines for the month
May | / | 0.13333 | 7 | / | 0.1 | 0.7 |  | May | 0.1 | 16.7 | 0.1 | 0.9
Jun | / | 0.46667 | 23.8333 | / | 0.43333 | 5.5333 |  | Jun | 1.2 | 64.4 | 1.1 | 15.6
Jul | / | 0.066667 | 4.9667 | / | 0 | 0.26667 |  | Jul | 0.1 | 8.9 | 0 | 0.3 | Maximum: for 1/2 hourly and daily periods use the highest value across all operational combustion lines for the month
Aug | / | 0.1 | 0.6 | / | 0.033333 | 0.16667 |  | Aug | 0.1 | 0.4 | 0 | 0.2
Sep | / | 0.23333 | 5.1333 | / | 0.16667 | 1 |  | Sep | 0.2 | 4.1 | 0.1 | 0.5
Oct | / | 0.13333 | 3.9 | / | 0.033333 | 0.23333 |  | Oct | 0.1 | 10.2 | 0 | 0.3
Nov | / | 0 | 0 | / | 0 | 0 |  | Nov | 0 | 0 | 0 | 0
Dec | / | 0 | 0 | / | 0 | 0 |  | Dec | 0 | 0 | 0 | 0
[8 empty] | Annual | 0.41667 | 636.6 | 0.28333 | 21.9
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A2 | Jan | 0.5 | 115.8 | 0.5 | 3.9
[8 empty] | Feb | 0.2 | 14.3 | 0.2 | 0.9
[8 empty] | Mar | 0.1 | 9.4 | 0.1 | 0.6
[8 empty] | Apr | 0.1 | 3.4 | 0 | 0.2
[8 empty] | May | 0 | 2.2 | 0 | 0.3
[8 empty] | Jun | 0 | 4.6 | 0 | 0.1
[8 empty] | Jul | 0 | 4.6 | 0 | 0.2
[8 empty] | Aug | 0 | 0.2 | 0 | 0
[8 empty] | Sep | 0.1 | 2.4 | 0.1 | 0.3
[8 empty] | Oct | 0.1 | 0.3 | 0 | 0.2
[8 empty] | Nov | 0 | 0 | 0 | 0
[8 empty] | Dec | 0 | 0 | 0 | 0
[8 empty] | Annual | 0.091667 | 115.8 | 0.075 | 3.9
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A3 | Jan | 0.3 | 29.6 | 0.2 | 1.3
[8 empty] | Feb | 0.1 | 8.9 | 0.1 | 0.3
[8 empty] | Mar | 0.3 | 81.4 | 0.3 | 3
[8 empty] | Apr | 0.2 | 5.1 | 0.2 | 1.9
[8 empty] | May | 0.3 | 2.1 | 0.2 | 0.9
[8 empty] | Jun | 0.2 | 2.5 | 0.2 | 0.9
[8 empty] | Jul | 0.1 | 1.4 | 0 | 0.3
[8 empty] | Aug | 0.2 | 1.2 | 0.1 | 0.3
[8 empty] | Sep | 0.4 | 8.9 | 0.3 | 2.2
[8 empty] | Oct | 0.2 | 1.2 | 0.1 | 0.2
[8 empty] | Nov | 0 | 0 | 0 | 0
Comments : | [7 empty] | Dec | 0 | 0 | 0 | 0
An indicated ELV value of zero in the table above means that no ammonia limit is set in the permit. | [7 empty] | Annual | 0.19167 | 81.4 | 0.14167 | 3
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A4 | Jan
Feb
Mar
Apr
May
Jun
Signed |  |  |  | Date | 2021-03-08 |  |  | Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2020 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A5 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0

## CO 95% 10 min
Annual Performance Report 2020 |  |  |  | Full Circle Generation Ltd
Monitoring of Carbon Monoxide (10-minute avg) |  |  |  | Whole Installation |  |  | See Notes in Cell S3 | Monitoring of Carbon Monoxide (10-minute avg) |  |  |  |  | Per Combustion Line |  | Notes: | Notes:
User to add logic to complete Whole installation, Table A5:H18. From the data in Per Combustion Line, Table K6:Q79, subject to No. of lines installed
mg/Nm3 | 10-minute Reference Periods |  |  |  | Daily Reference Periods
2020 | 95%ile 10-min avg CO ELV | 95%ile 10-min avg maximum | Monthly CO 10-min avg mean | 10-min avg maximum | Daily CO ELV | Monthly daily mean | Highest daily maximum |  | 2020 | mg/Nm3 | 95%ile 10-min avg maximum | Monthly CO 10-min avg mean | 10-min avg maximum | Monthly daily mean | Monthly daily maximum
Jan | 150 | 128.6667 | 1.7333 | 955.6667 | 50 | 1.4333 | 11.4667 |  | A1 | Jan | 0.8 | 0.3 | 2.7 | 0.2 | 0.5
Feb | 150 | 3.5667 | 0.76667 | 424.7667 | 50 | 0.73333 | 4.4333 |  |  | Feb | 1.9 | 0.9 | 458.2 | 0.9 | 4.6
Mar | 150 | 254.8 | 2.3 | 1173.1333 | 50 | 3.2 | 36.8667 |  |  | Mar | 758.7 | 5.1 | 2177.5 | 7.4 | 86.2 | Whole Installation table A5:H18:
Apr | 150 | 4.5333 | 0.8 | 682.5 | 50 | 0.83333 | 7.2667 |  |  | Apr | 0.9 | 0.6 | 554.1 | 0.6 | 4.1 | Mean: for 10-min and daily periods use average of all operational combustion lines.
May | 150 | 4.6333 | 0.8 | 904.9667 | 50 | 0.86667 | 11.3 |  |  | May | 10.4 | 1.2 | 1500.1 | 1.3 | 18.5
Jun | 150 | 43.8 | 0.53333 | 461.2667 | 50 | 0.43333 | 2.1667 |  |  | Jun | 3.9 | 0.7 | 847.4 | 0.7 | 4.9
Jul | 150 | 75.1 | 1.6 | 589.0667 | 50 | 1.9 | 11.1333 |  |  | Jul | 0.9 | 2.4 | 1152.2 | 2.1 | 9 | Maximum: for 10-min and daily periods use the highest of all operational combustion lines in any month.
Aug | 150 | 0.73333 | 0.26667 | 9.4333 | 50 | 0.16667 | 0.46667 |  |  | Aug | 0.8 | 0.3 | 1 | 0.2 | 0.4
Sep | 150 | 1.7333 | 0.46667 | 187.2333 | 50 | 0.4 | 1.8333 |  |  | Sep | 0.8 | 0.5 | 290.2 | 0.4 | 2.7
Oct | 150 | 2.5667 | 0.6 | 241.3667 | 50 | 0.53333 | 3.3333 |  |  | Oct | 4 | 0.9 | 706.3 | 0.8 | 8.6
Nov | 150 | 0 | 0 | 0 | 50 | 0 | 0 |  |  | Nov | 0 | 0 | 0 | 0 | 0
Dec | 150 | 0 | 0 | 0 | 50 | 0 | 0 |  |  | Dec | 0 | 0 | 0 | 0 | 0
[10 empty] | Annual | 65.2583 | 1.075 | 2177.5 | 1.2167 | 86.2
[9 empty] | 2020 | mg/Nm3 | 95%ile 10-min avg maximum | Monthly CO 10-min avg mean | 10-min avg maximum | Monthly daily mean | Monthly daily maximum
[9 empty] | A2 | Jan | 15.8 | 3.3 | 1705.6 | 3.3 | 26.8
[10 empty] | Feb | 5.3 | 0.9 | 340.2 | 0.8 | 4.6
[10 empty] | Mar | 1.5 | 0.8 | 663.3 | 1.2 | 13.4
[10 empty] | Apr | 8.5 | 0.6 | 617.1 | 0.7 | 6.5
[10 empty] | May | 1 | 0.5 | 444.4 | 0.5 | 4.5
[10 empty] | Jun | 126.1 | 0.5 | 475.7 | 0.2 | 0.7
[10 empty] | Jul | 0.5 | 0.2 | 280.3 | 0.2 | 2.2
[10 empty] | Aug | 0.3 | 0.1 | 0.6 | 0 | 0.1
[10 empty] | Sep | 1.3 | 0.3 | 45.7 | 0.3 | 1.7
[10 empty] | Oct | 1.6 | 0.4 | 7.7 | 0.3 | 0.6
[10 empty] | Nov | 0 | 0 | 0 | 0 | 0
[10 empty] | Dec | 0 | 0 | 0 | 0 | 0
[10 empty] | Annual | 13.4917 | 0.63333 | 1705.6 | 0.625 | 26.8
[9 empty] | 2020 | mg/Nm3 | 95%ile 10-min avg maximum | Monthly CO 10-min avg mean | 10-min avg maximum | Monthly daily mean | Monthly daily maximum
[9 empty] | A3 | Jan | 369.4 | 1.6 | 1158.7 | 0.8 | 7.1
[10 empty] | Feb | 3.5 | 0.5 | 475.9 | 0.5 | 4.1
[10 empty] | Mar | 4.2 | 1 | 678.6 | 1 | 11
[10 empty] | Apr | 4.2 | 1.2 | 876.3 | 1.2 | 11.2
[10 empty] | May | 2.5 | 0.7 | 770.4 | 0.8 | 10.9
[10 empty] | Jun | 1.4 | 0.4 | 60.7 | 0.4 | 0.9
[10 empty] | Jul | 223.9 | 2.2 | 334.7 | 3.4 | 22.2
[10 empty] | Aug | 1.1 | 0.4 | 26.7 | 0.3 | 0.9
[10 empty] | Sep | 3.1 | 0.6 | 225.8 | 0.5 | 1.1
[10 empty] | Oct | 2.1 | 0.5 | 10.1 | 0.5 | 0.8
[10 empty] | Nov | 0 | 0 | 0 | 0 | 0
Comments : | [9 empty] | Dec | 0 | 0 | 0 | 0 | 0
Environment Agency explanatory note: The 10-minute average ELV is based on the “95th percentile”. In this case this means that 95% of the 10 minute averages in the relevant 24-hour period (i.e. 137) must be below 150 mg/Nm3, and 5% (i.e. 7) are allowed to be any value above 150 mg/Nm3. Whilst we expect operators to minimise CO emissions at all times, it is perfectly acceptable for the value of the maximum 10-minute average to be above 150 mg/Nm3, provided the 95th percentile ELV has been met for that period. | [9 empty] | Annual | 51.2833 | 0.75833 | 1158.7 | 0.78333 | 22.2
[9 empty] | 2020 | mg/Nm3 | 95%ile 10-min avg maximum | Monthly CO 10-min avg mean | 10-min avg maximum | Monthly daily mean | Monthly daily maximum
[9 empty] | A4 | Jan
Feb
Mar
Apr
May
Signed |  |  |  |  | Date | 2021-03-08 |  |  |  | Jun
Jul
Aug
Sep
Oct
Nov
Dec
[10 empty] | Annual | #DIV/0! |  | 0 | #DIV/0! | 0
[9 empty] | 2020 | mg/Nm3 | 95%ile 10-min avg maximum | Monthly CO 10-min avg mean | 10-min avg maximum | Monthly daily mean | Monthly daily maximum
[9 empty] | A5 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[10 empty] | Annual | #DIV/0! |  | 0 | #DIV/0! | 0

## Sch 1
Annual Performance Report 2020 | [6 empty] | Full Circle Generation Ltd
Residue Quality Monitoring Requirements
Schedule 1 Notifications | [5 empty] | Year: |  | 2020
No. | Boiler / Parameter |  | Period |  |  | Duration |  | Concentrations
Sch 1 No. | Line | Parameter | Reference Period | Date | Start Time | 30 minute | 10 minute | 30-min (mg/Nm3) | 10-min (mg/Nm3) | Daily (mg/Nm3)
1 | 2 | TOC | 30 min average | 2020-01-15 | 22:59 | 30 |  | 53.2
2 | 3 | CO | 10 min & 30 min average | 2020-01-15 | 20:00 | 30 | 10 | 510.6 | 369.4
3 | 3 | TOC | 30 min & daily average | 2020-01-16 | 21:30 | 30 |  | 166.7 |  | 24.88
4 | 2 | TOC | 30 min average | 2020-03-11 | 4:59 | 30 |  | 75.7
| 2 | HCl | 30 min average | 2020-03-11 | 4:59 | 30 |  | 281.2
5 | 1 | SO2 | 30 min average | 2020-03-12 | 1:59 | 30 |  | 605.6
6 | 3 | HCl | 30 min average | 2020-03-16 | 22:29 | 30 |  | 143.5
| 3 | TOC | 30 min average | 2020-03-16 | 22:29 | 30 |  | 52.7
7 | 1 | CO | 10 min & 30 min average | 2020-03-17 | 10:59 | 30 | 10 | 971 | 758.7
| 1 | SO2 | 30 min average | 2020-03-17 | 12:29 | 30 |  | 672.5
| 1 | TOC | 30 min average | 2020-03-17 | 12:29 | 30 |  | 78.2
8 | 3 | SO2 | 30 min average | 2020-03-17 | 6:59 | 30 |  | 236.3
9 | 1 | CO | 10 min average | 2020-03-26 | 19:29 |  | 20 |  | 137.4
| 1 | SO2 | 30 min average | 2020-03-26 | 22:59 | 120 |  | 374 / 880.8
| 1 | HCl | 30 min average | 2020-03-26 | 23:29 | 30 |  | 73.8
| 1 | TOC | 30 min average | 2020-03-26 | 22:59 | 120 |  | 145.7 / 11224.4
10 | 1 | TOC | 30 min average | 2020-03-27 | 0:29 | 30 |  | 179.5
11 | 1 | PCDD/PCDF | Extractive | 2020-04-22 | 8:18 |  |  | 0.177 ng/m3
12 | 3 | SO2 | 30 min average | 2020-04-29 | 16:59 | 30 |  | 497.6
13 | 1 | SO2 | 30 min average | 2020-05-17 | 11:59 | 30 |  | 283
| 1 | TOC | 30 min average | 2020-05-17 | 11:59 | 30 |  | 106.4
14 | 1 | SO2 | 30 min average | 2020-06-02 | 14:59 | 30 |  | 526.8
| 1 | HCl | 30 min average | 2020-06-02 | 14:59 | 30 |  | 67.7
| 1 | TOC | 30 min average | 2020-06-02 | 14:59 | 60 |  | 46.2 / 70.3
15 | 2 | CO | 10 min average | 2020-06-04 | 18:59 |  | 10 |  | 126.1
16 | 1 | HCL | 30 min average | 2020-07-26 | 18:59 | 30 |  | 74.1
17 | 1 | SO2 | 30 min average | 2020-07-27 | 18:29 | 30 |  | 214.9
18 | 1 | SO2 | 30 min average | 2020-10-05 | 13:59 | 30 |  | 413.7
Count of Sch 1s: | No of breaches: |  |  |  |  | Total No. of Hours | Total No. of Minutes
18 | 28 |  |  |  |  | 16 | 50
Signed |  |  |  | Date | 2021-03-08